## READ FIRST
All Modifications to this document must be approved through CIB for EntelliGuard
Additional Considerations
1 | UL, ANSI, CSA, IEC File Updates
2 | ATE Update with Test Controls Inc (TCI) and IES and spec (10111948P1) as needed
3 | Option Dispenser Update (Electronics Team)
4 | Mfg Plant Quality Systems: SJV, Bielsko Biala, Vega Baja, Electronics City, Belo
5 | Label Database/Printing System Updates (Systems Team/MFG)
6 | Rulestream Rules, 10101883P1 (Kirk Thompson, MITR)
7 | MWP BOM's
8 | Commercial Documents updated (Product Management)
9 | SJV shop order decoder 11112222P1 in the manufacturing docs under any White Good
10 | Notify Sales Configurator Team - Gary Schulz, Pavani Arakula, Divyangkumar Varmona, Madhu KUM Uppaluru
11 | IEC Decoder 10103289P1
12 | Burlington Req. Eng. for Rulestream - Bill Bice
13 | Req Engineering - Kevin Brueck, Nilesh Sonar
14 | Application Engineering - Randy Crow
Distribution List
Product Management | Daniel Sosa | Sosa, Daniel (GE Energy Management) <daniel.sosa@ge.com>
Product Management | Viktoriya Moroz | Moroz, Viktoriya (GE Energy Management) <viktoriya.moroz@ge.com>
Systems Manager | Glen Sisson | Sisson, Glen (GE Energy Management) <Glen.Sisson@ge.com>
Systems Manager | Narayanan, J | Narayanan, J (GE Energy Management) <Janakiraman.Narayanan@ge.com>
Systems Engineer | Ryan Sparrow | Sparrow, Ryan (GE Energy Connections) <Ryan.Sparrow@ge.com>
Systems Engineer | Jacek Urbanowicz | Urbanowicz, Jacek (GE Energy Management) <Jacek.Urbanowicz@ge.com>
Systems Engineer | Fang Hua | Fang, Hua 2 (GE Energy Management) <Hua.Fang2@ge.com>
Quality Engineer | Janusz Rasinski | Rasinski, Janusz (GE Energy Management) <Janusz.Rasinski3@ge.com>
Post Sales Service | Bill Martin | Martin, William (GE Energy Management) <William.Martin2@ge.com>
Post Sales Service | Steve Pollpeter | Pollpeter, Steve (GE Energy Management) <Steve.Pollpeter@ge.com>
Post Sales Service | Merle Coffey | Coffey, Merle (GE Energy Management) <merle.coffey@ge.com>
Quotes | Shari Martin | Martin, Shari (GE Energy Management) <shari.martin@ge.com>
Quotes | Ted Rolof | Rolof, Theodore (GE Energy Management) <theodore.rolof@ge.com>
RUE System Architect | Kirk Thompson | Thompson, Kirk (GE Energy Management) <kirk.thompson@ge.com>
AME | Octavio Cortes Flores | Cortes Flores, Octavio (GE Energy Management) <Octavio.CortesFlores@ge.com>
AME | Rajesh Babu | G, Rajesh Babu (GE India) <RajeshBabu.G@ge.com>
Requistion Engineering | Kevin Brueck | Brueck, Kevin (GE Energy Management) <kevin.brueck@ge.com>
Requistion Engineering | Nilesh Sonar | Sonar, Nilesh (GE Energy Management) <nilesh.sonar@ge.com>
Requistion Engineering | Dave Naugle | Naugle, David (GE Energy Management) <david.naugle@ge.com>
Rulestream for Req. Eng. | Bill Bice | Bice, Bill (GE Energy Management) <bill.bice@ge.com>
Applications Engineering | Joe Vetter | Vetter, Joseph (GE Energy Connections) <joseph.vetter@ge.com>
SAP Configurator Team | Gary Schulz | Schulz, Gary (GE Energy Management) <gary.schulz@ge.com>
SAP Configurator Team | Pavani Arakula | Arakula, Pavani (GE Energy Management, Non-GE) <Pavani.Arakula@ge.com>
Manufacturing Engineer | Slawomir Bieronski | Bieronski, Slawomir (GE Energy Management) <slawomir.bieronski@ge.com>
Material Specialist | Piotr Zaczynski | Zaczynski, Piotr (GE Energy Management) <Piotr.Zaczynski@ge.com>
MSO - Burlington | Steve Reeves | Reeves, Steven (GE Energy Management) <Steven.Reeves@ge.com>
IEC Product Manager | Arvind, T S | Arvind, T S (GE Energy Connections) <TS.Arvind@ge.com>

## Revision History
Rev. Number | Date | CR # | Increment | Description | By
1 | 2008-07-07 | R0824892 |  | First Release | Anurag
2 | 2009-03-04 | R0903447 |  | "For GACB nomenclature update for UL/NEMA par Darrin Bock" | Darrin
3 | 2012-08-13 | R1208768 |  | Adding new 6th digit, "S", for GE drawout Frame 2 breakers 2000A and below. Additionally, adding numerous changes that have been made over time to document but not driven through w/ a CR. | Seabrook
4 | 2013-05-02 | R1308779 |  | 1. Modifying Ratings for EntelliGuard L 2. Modified Lock Options 3. Modified 60 msec UVR | Delfino
| 2013-05-22 |  |  | 1. Added C & D EntelliGuard L 2. Added RTC contacts NC (cat codes & Nomenclature) 3. Added D on EntelIiGuard L cassettes | Thomas
| 2013-05-28 |  |  | 1. Added mounted Ronis and Profalux locks (only as accessory cat number) | Thomas
5 | 2013-01-14 | R1332686 | 1 | 1. Made X, Y, Z 6th digit characters UL & ANSI vs. UL only | Delfino
|  |  | 2 | 2. Removed GTU nomenclature and referenced p/n
|  |  | 3 | 3. Added GCPSB/R on Accessories Page
|  |  | 4 | 4. Added second digit "P". Uncaptured change from ATE
|  |  | 5 | 5. Added MiniGuard Accessories
|  |  | 6 | 6. Added SAP #'s tab
|  |  | 7 | 7. Added 200kA ratings
|  |  | 8 | 8. Changed cassette 10th digit for Ronis and Profilaux, Updated IEC 13th digit, Added IEC Retrofill | Thomas
|  |  | 9 | 9. Adding Fusible EntelliGuard R nomenclature | Delfino
|  |  | 10 | 10. Clarifying 30VDC for ST and UVR.
|  |  | f | f. Formating and Validating to UL, ANSI, and IEC files. (PENDING M.THOMAS INPUT)
|  |  | g | g. updated availability columns in digit 14
|  |  | i | i. Updated interruption tiers for EGT and EGL. Turned on X and Y for IEC in 6th digit. Added AEG Branded digit 1 | Thomas/Delfino
|  |  | j | j. Removed "future" in digit 6 on characters V, W | Delfino
|  |  | k | k. Updated Close Coil digit B for IEC 48V
|  |  | l | l. Updated voltages for IEC ratings in 6th dig.
|  |  | m | m. updated READ FIRST tab for Sales configurator team
|  |  | n | n. added character "7" to digit 13 for 2 NO BALO
|  |  | p | p. updated w/ Janusz's comments on IEC EGG, EGL, and EGT (see Red Text w/ Yellow Background) | Janusz
|  |  | q | q. updated "W" interruption tier for Entellisys | Delfino
6 | 2013-01-23 | R1400376 | a | a. removing no rear terminations for IEC. Adjusting IEC cassette digits. B. adding 400A ANSI breaker availability in dig 3,4 and adding 1000A c. updated AKD5 cassettes and breaker digit 5,6. turned on dig. 5="n" and "D", and Digit 6 = "1" or "2" or "3" for cassette. Updated the interruption tiers for EGL in digit 5 for switches. Was "R" ... updated to "S" for F1 Added digits 1,2 headings for table in digit 5 Added DC Ratings for IEC breakers Added/Removed Available IEC constructions for GH, GJ, GK and EGL Removed Frame 3 type GH's Added "D" for digit 20, 225A rating plug d. added GF and GFDB on E02 IEC TU Updated 600Vdc rating on UL489b tab Updated 220Vdc for IEC motors, digit 7 Updated digit 8, removing CCC's over 250Vac as the switch is not rated for this. f. Added Drawout only for IEC type GH, GZ, GK Removed IEC cassette construction type horizontal terminations Added note in digit 8 for Electric Close Switch Removed X from digit 10 in NI section Digit 11, made A available only for IEC Digit 13, added note for switches Digit 5, removed 2000, 2500A LJ switches Removed 4P right availability for EGL on Digit 6 Dig 16-18 IEC, added note for XXX only available for switches and made to match TUtypes.xlsx Dig. 13 added character 7 for internal sale only Dig 15. Added note for cables Dig 12. Note added for Coil signalling and RTC contacts Dig. 13, Note added for thru TU require comm. Dig 7, removed character K for IEC Dig 12, removed character 3, not valid per UL file Dig 14, B and 5 removed for ANSI/UL g. Dig 2. cassettes only GG and GH type cassettes Dig. 3 Cassette updated table for EGG, EGL, EGT availability Cassette removed current ratings not applicable based on dig. 5 Dig. 5 cass. Updated table to match breaker table calling out types (GU, GB, etc) Updated IEC voltages 1200N removed F1 M types removed. 16M and 20M added. Removed 08M for F2 Dig. 7 cass. Added columns for EGG, EGL, EGT Dig 9 Cass Removed U, R, and P Dig. 11. Cass. Removed all digits for EGL and EGT except "X" Dig. 12 Cass. Removed 3 for IEC EGG. Dig. 13 Cass. "7" removed for all poles. GE Services only. D, K, G, added for EGL Dig. 14 Cass. Removed "B" and "5" for EGG h. Dig 5 Cass. 1200N removed, added 16M and 20M. Removed 08M Dig 9,10,11 Removed "U", added "R" and "P" Dig 16-20. added note for ** not UL approved Dig. 3,4,5 Cass. Removed 1200A ANSI switch i. Dig 5. F3, 3000A UL switch removed, add 1200N Switch, Add 800-2000A UL F2 switch, Added UL Switch B tier, F2 ANSI Switch M tier 800,1600, 2000, F3 ANSI Switch B tier, added note for W tier w/d only, Added note for S and P type - 3 pole only Dig 5 cass, removed 08S types j. Dig 5. Removed 12N ANSI Switch Dig 5. Added 12N UL Switch Dig 5. Added 30B UL Switch Dig 5. Cassette: Added B interruption for UL489 Switch. Removed 30L and 60L for UL489 switch Added 30B and 60B. Dig 5 Cassette: Added 3 pole only note for S and P k. Dig 9 and 11: Added non continuously rated shunt release l. Dig 5 breaker and cass. Added * footnote UL PV switches, dig 3,4 : removed 1600. Same for cassettes Dig. 9 cassettes: added "U" for E+E51GT Dig 6 - added 2, 5 for EGT breaker only. Note that switch is not available. Dig 7 - added B, C, F, G, M, N for EGT Dig 8 - added D, H, L, M, P, Q, R, T, U, W, Y for EGT Dig 9 - added D, H, L, for EGT Dig 10 - added 4, 8, Y for EGT Dig 13 - added 3,4,5,6,F, S, J, Y for EGT Added SJV decoder on READ FIRST tab, 10103289P1 Updated EGL and EGT cassette offering in dig 5 Dig 3,4 updated "Yes" for UL CB and non auto CB for 5000A Dig 5, Type GA, removed 12P Dig. 6 removed character 2, 6 for IEC EGG Dig 5 Cassettes added GU30H m. Dig 5 GZ switch removed M added H for F2 EGL type GJ updated availability to R and C for F1 and F2, respectively Dig 6. Added 4 pole right available for IEC, added note not for sale in Europe. n. Dig. 5. added tiers U and Y UL DC Switches, removed 1200A, added 1600A. Error in rev 6L Digit 9 removed characters 3,4,8,W, Y as they are not released. Additions for frame 2.5 in digit 5 and updates to Retrofill tabs (breaker/cass) for EGR 2000A o. Removed 1250A EGT cassette. Digit 5 - Updated IEC Icm ratings to peak Ka's and added isolator column Retrofill and Retrofill Cassette Tab - Dig. 6 Updated applicability by gear type Digit 5 Breaker and Cassette - added V interruption tier (Projected release for production Q4 '16) Digit 5 - 1000Vac/dc added frame restriction notes Digit 14 - restructured to add Mounted lock cylinders p. Digit 14 - updated A, G, H to S, 6, 7, respectively q. Digit 5 - removed 2500, 3000, and 3200A for "V" interruption tier r. Digit 15 - added clarification for character "1" for type D interlocks s. Digit 5 - Removed 1000V ratings as they are not qualified Added close and latch ratings and clarification for Non-Auto CB and switch ratings t. UL489B tab digit 5 - added cassette variant Dig 14 Mounted Keylock INCOMPLETE u. Changed note syntax since it was illegible in some cases Added AEG breaker and cassette variant tabs Dig 5 added clarification for GP16HS and GY16HS and ratings, updated close and latch ratings, changed heading on Icm for breakers/switches w/MCR Dig 6 added note for A, B, C Removed GECP note on digit 8 Dig 12 - Character 3 turned on for EGL v. Dig. 5 Replaced IEC 1000Vac ratings for Env. 1 and Env. 2 only. Cassette Dig 5 - added 50M Env. 3 cassette w. Updated rev history for u. and v. Added note 2 for digit 14 on applicability of key interlocks Retrofill tab. Added note that all are drawout. Reformatted Digit 5, added notes for non-standards UL/non-UL, removed unused characters Cassette: Added U and Y in digit 5, Updated 1000Vac and notes Dig 15. updated number of cables req'd for Type B and C and added header for reference table of cables. x. Retrofill tab. Added AKD type Swgr, removed AKR30S from AKD6 Retrofill Cassette Tab - carried over changes from lines above in Retrofill breaker tab. Added 1000A in dig. 3,4. Added UL approved comb. table under dig 5 y. Breaker mounted and cassette mounted keylock cylinders added z. Dig 13 - added double Bell Alarm characters 8, 9, Q and unrestricted for GE Internal only. Made "M" available for EGT. Reordered table for clarity Dig 11 - Updated EGG IEC none option (was not available prior) Dig 8 - updated EGT none option (was not available prior), Adjusted the voltage rating for "A" for IEC to 24Vdc, Adjusted applicability for "B" for EGG IEC and EGT, 220-240Vac/dc for "G", 250Vdc,250-277 Vac for "K", similar for CCC's Dig 5 - Removed IEC DC ratings as they have not been tested. Dig 9 - Updated 60Vdc for "D", added applicability for option "B" for EGT Dig 10 - Updated voltage ratings for 4,5,8,9 and applicability for EGT for 9 aa.Cass. Dig 7. - added X option for no rear terminations Dig 14. Added mounted lock cylinder option Dig 5, note 3 updated F1/2 to F2/3 Retrofill Cass. Greyed out everything in Dig 2 except 0,1,4. Dig 6 updated applicability notes to be based on breaker vs. cassette first 5 digs. Retrofill Dig. 6 - Changed AKD 6/8 to AKR Only in description col. Added "yes" for "X" to AKD6 Dig. 2 - Added "C" for EGL ab. Digit 2 clarified description for C for EGL Cassette tab - Removed 1000Vdc ratings Dig 13 - Removed double BALO options from EGG - IEC and EGT Retrofill Tab - Clarified AKD6 AK25 and AK50 are "R1" prefixes Dig 2. added note 6 Retrofill Cassette Variant - removed XX since not in UL file Cassette Tab - Removed note 2 for H and note 3 for M since there are no Env. 2 and Env. 3, respectively. ac. formatted revision history tab ad. Dig. 2 - Changed C for EGL to I ae. Dig 13. 2 NO BALO for ANSI af. Dig 5. removed Y for ANSI and replaced with U ag. Added note 4 for digit 12 ah. Digit 16-19 IEC, GTU, H23, H36, H37 added J switchable and ST non-switchable, removed ST Switchable H51-62 removed RELT S05, 09 removed RELT Added digit 16 character "P". All characters for digits 17,18 are based on the existing Tab 16-20 UL_ANSI GTU added LM, LN, LP Tab 20 to 18 UL_ANSI conversion, digit 16, added M, N, P ai. Updated digit 11 for OFLO Updated Retrofill Variant Digit 2 descriptions for chars. 4-6 Made updates on Retrofill Variant tab for ME07+E51 aj. Retrofill Variant - Dig 5. Updated description for "U" in AKD6 and AKD8 Retrofill Varian - Dig 2, 5, 6 added Entellisys proposal NOT COMPLETE YET 4/24 Cassette tab, added note 1 in digit 9 Digit 12-15, dig 14, note 2 added clarification for drawout breakers. Retrofill variant dig 2,3,4,5,6 updates for AKD10 Entellisys and secondary disconnect types Retryfill variant dig. 2 added character "H" for AKD 8 horz lower stud Dig 1-6, 5th digit, uprated "K" at 500V and 690V to 55ka and 50ka, respectively. Also added note 11 and updated Ics ratings. Dig 14, Updating description for Bell Alarm from "NO" to "Form C" Retrofill Dig. 6 added clarification to description for X as it applies only to AKD6 AK25/50. Removed AKR Only note from 1,2,3,4 ak. dig. 20 clarified note 1 as X is not allowed for breakers. al. Retrofill tab, digit 5, AKD10 area, Updated WPX20 to WPS20 am. Digit 14, removed E, F, M, N as mounted castell locks are not provided an. Digit 5 adjusted IEC H type to 85kaic for Icu rating on envelope 2 only (referenced to note 2), removed 50kA rating at 1000Vac, added note 12 on 35ka (for env.1 only), Moved note 4 to header Retrofill Variant Digit 6, added (AKR breakers only) note to characters 1,2,3,4 Retrofill Cassette variant Digit 2, removed gray fill and "future" note for 2000A. Digit 6, clarified applicability for character "1", Digit 6 updated description for character 3 from 12 pin to D block, removed availability for character "3" from AKD6 | Delfino - SAP configurator team inputs
b
c
d
f
g
h
i
j
k
l
m
n
o
p
q
r
s
t
u
v
w
x
y
z
aa
ab
ac
ad
ae
af
ag
ah
ai
aj
ak
al
am
an
|  |  | ao | ao. Digit 6 Updated the Icu for ANSI character U to 130ka
|  |  | ap | ap. Retrofill Variant Digit 5, for AKD5 removed V and updated description for T to include AKJT50 and AKJT50H, also updated description for N to include AKJ50
|  |  | aq | aq. Updated Read First Tab to include Burlington/India Req Eng. and Application Teams
|  |  | ar | ar. Read First Tab - Updated Distribution List
Retrofill Tab - Updated Digit5 for Digit 2 = R (ME07)
Cassette Tab - Marked IEC Dig 7 = X as "Future".
Retrofill Variant Tab - Updated frame sizes for ME07/MET07 digit 5
Dig. 9 - Added applicability column for ME07 Retrofill: No Remote Reset available, otherwise EGG IEC
Dig 14. - Added applicability column for ME07: X only
Dig. 12 - Added applicability column for ME07: 2,3,4,6,8 only
Dig 16-19 - Added applicablity column for EGR: Copied from EGG and/or EGT
Dig7-11, 12-15, 16-19 (IEC) Updated applicability headings to consistent with the addition of the EGR ME07, otherwise EGR above IEC holds true.
Retrofill Variant Dig. 2 - modified descriptions for 2, 5,6,7,8
Dig. 10 - Removed 30V UVR for IEC
Dig. 5 - Added note 7 (3 pole only) for all U types (narrow frame)
Dig 12. Updated note 4 to not allow character 4,8 when Env. 1 SSD
Dig 15. Updated applicability to remove EGR ANSI availability.
Dig. 2,6,12,18,19 added general note on affect of SD assignment and referenced decoder docs 11112222p1 and 10101883p1
Cassette Tab - removed 1250A EGT, removed EGL 20S, 25S, added 20N, 25N w/ notes 11 and 12, respectively
Retrofill Variant - Dig 2, removed H as 6 is now updated for OEM and GE
Retrofill Variant - Dig 5, E and F for ME07 retrofill, updated Icw from 55 to 50
Dig 8. Removed 30Vdc CC and CCC for IEC markets as there is no SKU for it in IEC decoder.
Dig. 9 added option X for IEC EGG, Added non-continuous shunts for EGT, added applicability columns for ME07
Dig 5. Note 4: Corrected spelling of "separators", it was missing "a rat"
Retrofill Variant Dig 5. Updated Icm values for ME07
Dig 10 - added ME07 applicability column
Dig 11 - added ME07 applicability column
Dig 12 - added ME07 applicability column
Dig 14 - added ME07 applicability column
Dig 15 - added ME07 applicability column
UL489B Variant - updated SC rating from 30kA to 125kA
|  |  | as | as. Dig. 5 Updated 2500A S and F for IEC EGG Created Retrofill Entellisys Tab Cassette - added Frame 2.5 options. Removed "Y" option for ANSI and changed to "U" Dig. 16-20 UL_ANSI - Dig. 19 added note 2 for internal ANSI 5000A and 6000A breakers Dig. 9 added note 1 "not available on switch" for remote reset Cassette Dig 9 Removed U and N for EGG as there is no design at the time. Retrofill Variant Dig 6 - added note 2 for ME07 variant. Digit 5 - added note 13 and 14, turned character "V" to future. Cassette - added 25H and 25F types for IEC, removed "Future" for X, digit 6, IEC Dig 6 - X, Y, Z for IEC now available! Right neutral now available for ALL of IEC. No more limitations for Europe. Dig 2 updated F2.5 descriptions for A, B, C, D
|  |  | at | at. Cass. Dig 8 added Yes for "X"
Dig 11 - removed character "2" for EGG IEC and ME07
Conversion 20 to 18, added "D" for 225A
Dig 14 - Added F and N
Dig 8 - Updated K and W voltage description to 380-415 Vac from 250Vdc, 250-277Vac. Updated H and U description for Voltage.
7 | 2015-11-23 | C014041 | a | Incremented revision | Schulz
Dig. 5 - Updated close and latch rating for "U". Added note 15 for EGL 40kA @690V Icu, Updated Icw @690V for C=50, N and D = 65
Dig 14. IN PROGRESS. Need to confirm with Daniel and Dev - changed F and N to large castell vs. 19mm
Cass. Dig 6 updated note 1 to include 2.5
Dig. 5 - Updated Icm for F type to 143 from 65
Dig. 5 For Brealer ANSI Close & Latch Added footnote [2] to Tier N and footnote [3] to Tier M
Dig. 5 For Cassette ANSI Close & Latch Added footnote [2] to Tier N and footnote [3] to Tier M
Dig. 7 for IEC Cassette; Removed EGT Vertical Bus and EGL No Rear copper
Dig. 1-6 added LJ20C and LJ25C (marked with yellow)
Dig. 1-6 moved F interrupting tier from below H to above N to give priority to Frame 1
Dig.14 moved F and N from Mounted Lock type Castelle (19mm) to Castelle (Large) (marked in yellow)
| 2016-04-16 |  | b | Dig. 14 removed B and 5 characters because 19mm part not available, per Devendra's email | Schulz
| 2016-06-01 |  | c | Dig. 8 Revised the close coil voltages to match UL approvals and the product label | Sparrow
8 | ? | C021591 | a | Cassette Tab: Changed S[7] to S for IEC rating as there are 4 pole S breakers in IEC | Schulz
Copied Notes 13, 14, 15 from Digits 1-6 Main tab to Cassette Tab for Digit 5 character table
Cassette Tab: Added [4] to IEC Digit F for 1000Vac
|  |  | b | Added 6000A ANSI model interrupt ratings and note 15 | Sparrow
Updated Retrofill Variant and Retrofill Cassette Variant for 3200A-5000A
Updated Digit 12: Corrected Coil Signalling Contact Heading and added note 5
Updated Digit 13: Added note 5 for double bell alarm
|  |  | c | Added 6000A ANSI Yes and note 1 for DIGITS 3, 4 Tab Digits 1-6 Main per Glen Sisson | Schulz
Added Note: See Digit 5….. For DIGITS 3, 5 Tab Digits 1-6
Reserved Digit 2 = 8 for “EntelliGuard T with MCR”
|  |  |  | Updated Digit 15 for Nuetral Ct adaptor | Swamy
|  |  |  | Updated Digit 2 = R (ME07) table on Tab Retrofill Variant | Schulz
Updated Dig 3,4 for Large Frame Retrofill
Added EGG Frame Size to Digit 5 Table for digit 2 = 1,2,3,4,5,6,7,8, Tab Retrofill Variant
Un Grayed Digit 2 Char 5 for Tab Retrofill Cassette Variant
Un Grayed Digit 3,4 Char 30,32,40 for Tab Retrofill Cassette Variant
Added Note [4] to Table 5 and for Char X ad 5 for Digit 2 - 1,4 Tab Retrofill Cassette Variant
Added Rating Plug Matrix tab
On tab DIGITS 12-15 ACC2, moved [3] from coil signalling items to the header
|  |  | d | Included EGG field for Retrofills digit 5 for AKD5,6,8 & 10 - Tab Retrofill variant | Swamy
Activated character 2 & 5 in digit 2, Activated 30, 32 and 40 for digit 3 & 4 - Tab Retrofill cassette variant
Added note no. 4 for digit 5 table - Tab Retrofill cassette variant
Updated applicability for Digit 3 & 4 for 30,32,40 & 50 on tab Retrofill variant
|  |  | e | Added AKD-6 LF col for Digit 6 in tab Retrofill variant | Swamy
Removed character 13 for IEC EGL for digit 3,4 in tab Digits 1-6 Main
|  |  | f | Added character 2 and 9 for digit 9, Added character Z for digit 10 - Tab Digit 7-11 ACC1 | Swamy
Removed character N in digit 11 - Tab Digit 7-11 ACC1
Added slot details for Digit 8,9,10 and 11 - Tab Digit 7-11 ACC1
| 2016-10-20 |  | g | updated character 4 and 5 for Digit 4 in Entellisys Retrofill variant worksheet | Swamy
| 2016-10-21 |  |  | Added "AEG branded retrofill (future)" to Digits1-6 Main and AEG (ME10) Variant Tab Digit 2 | Schulz
| 2016-10-26 |  | h | Put back character 13 for IEC EGL for digit 3,4 in tab Digits 1-6 Main | Schulz
| 2016-10-26 |  |  | Removed ENTG L and T 1250A Cassettes on Digit 3&4 Table and Digit 5 Table in Cassette tab
| 2016-10-26 |  |  | On Cassette tab remove frame 1 cassette for S type GW as that does not exist
| 2016-10-26 |  |  | Clarified GJ, GK, GW, GZ, LJ, G7 usage on Cassette tab
| 2016-10-26 |  |  | On Cassette tab remove frame 1 for H type GJ as no such breakers exist.
| 2016-10-26 |  |  | On Cassette tab remove frame 2 for Type E in the GJ areas
| 2016-10-26 |  |  | Add character 6 for Digit 4 in Entellisys Retrofill variant worksheet | Octavio
| 2016-10-26 |  |  | Add character 6 for the 480V OFLO and change the descriptions for the character 2 and 9 in the Digits 9 general nomeclature.
| 2016-11-08 |  |  | Updated Character 15 to include the mechanical interlock option | Sparrow
| 2016-11-17 |  | i | Updated Digit 15 to include Neutral Adapter per Ryan Sparrow | Schulz
| 2016-11-23 |  |  | Showed AKD6 LF secondary disconnect - Digit 6 limitation - Tab Retrofill Variant | Swamy
| 2016-12-08 |  |  | AMMENDED EGL CASSETTE TO NO REAR COPPER CONFIGURATION | ARVIND
| 2016-12-09 |  | j | Update Entellisys Variant Tab: Added note 2 to Digit 8 as follows: NI option includes the Hidden-On Button | Sparrow
| 2016-12-09 |  | k | Update Retrofill Variant Tab: Corrected Interrupting Rating for 2000A Digit 2=1,2,4 or 5 to 65/65/50 65/65/50 65
| 2016-12-16 |  | m | Added additional condition for C block (72 point) secondary disconnect - Tab Retrofill Variant | Swamy
9 | 2017-01-10 | C026566 | a | On Retrofill Cassette Variant: Removed Char 4 on Digit 6; Added AK75, AK100, AKR75 and AKR100 to Char 2 for Digit 6 | Swamy
| 2017-03-01 |  | b | Digit 6: Please move foot note (2) from the GT column to the EG-G IEC column, Marked "YES" on EG-L 4 pole OEM Neutral on right - DO and Stationary | Sparrow
| 2017-03-07 |  | c | Digit 16-19, IEC GTU: Added column AD "OV on ZSI out", Added Row 79 option "63" for digits 17 and 18
| 2017-04-10 |  | d | Digit 1-6: Added ANSI C37.13/UL1066 E-Type Frame 3 - 4000A and 5000A
10 | 2017-05-04 | C034249 | a | Cassette tab: Update digit 9 - Removed options "T" and "U" for all | Sosa
| 2017-05-18 |  | b | Update Tab Digits 1-6 Main: Corrected Digit 3/4 to show 6000A EG available for ANSI | Sparrow
| 2017-06-14 |  | c | Digits 12-15 ACC2: Digit 14 - Added note 3 for PB Padlock, Digit 15 - Added note 9 for Hidden On. These 2 options are conflicting
| 2017-07-21 |  | d | Digits 7-11 ACC1: Digit 9 - Removing letters 3, 4, 8, W and Y and using for Command Shunt Release - Pending addition details on the applicable products and approvals
| 2017-07-31 |  | e | Digits 1-6 Main: Update IEC Tier "M" Icu rating from 85/100 to 100. Note 3 now only applies to Icw rating
| 2017-09-15 |  | f | Digits 1-6 MAIN: Add Digit 5 "T" Interruption Tier for 800-2000A 4P 1500V DC switches; add 800-2000A FR2 version switches to Interruption Tier "N"
| 2017-09-27 |  | g | Digits 1-6 MAIN: Digit 5 add option for 1200A Type "P" FR1
|  |  | h | Digits 7-11 ACC1: Obsoleted GCCC voltage options 60 VDC and 208 VAC; Added Note 1 to Digit 8 for Command Close Coil
11 | 2017-10-04 | C039378 | a | Digits 1-6 Main: Updated Digit 2 option "I" to remove the note 6 superscript next to Yes and crossed out note 6 below Digits 1-6 Main: Updated Digit 5 IEC Breaker columns LG to LG or LI | Sparrow
| 2017-10-10 |  | b | Digits 7-11 ACC1: Reversed obsoleted GCCC voltage options 60 VDC and 208 VAC | Sparrow
| 2017-10-25 |  | c | Digits 1-6 Main: Updated Note 17 to show Digit 6 options "3" and "6" only for 1500VDC models Digits 16-19, IEC GTU: Updated digit 17&18 table to include GT-H/GT-N for EGL LI version only | Sparrow
| 2017-10-26 |  | d | Digits 1-6 MAIN: Add Digit 5 "N" Interruption Tier for 800-2000A (Future option) | Sparrow
| 2017-11-01 |  | e | Digits 7-11 ACC1: Add note 3 to Digit 9 Command Shunt Release | Sparrow
12 | 2018-01-30 | C054003 | a | Digits 16-19, IEC GTU: Remove "Yes" from EGL column for P-Type trip units | Sparrow
| 2018-03-19 |  | b | Digits 12-15 ACC2: Added note 10 to Digit 15: Neutral CT Adapter requires a trip unit with Ground Fault | Sparrow
| 2018-05-07 |  | c | Digits 7-11 ACC1: Added [1] next to the Command Close Coil heading to reference note 1; Removed Future box around command shut release Digits 1-6 MAIN: Added Future BOM around the 4000A Type GJ Interrupting tier "T"; Added note to Digit 5: [19] Tier "E" ANSI 4000A & 5000A breakers are restricted to Saudi only | Sparrow
| 2018-05-08 |  | d | Digits 1-6 MAIN: Updated Interruption Tier "W" 1/2 sec rating from 85kA to 100kA. Approved by UL project 4788411503 | Sparrow
| 2018-05-17 |  | e | Digits 1-6 MAIN: Removed tab hyperlink from Digit 1 = "R"; Updated Digit 1 Note 1 to include tab hyperlinks to AK_AKR_WP Retrofill and M-Pact Retrofill Retrofill Variant: Renamed to AK_AKR_WP Retrofill Variant M-Pact Retrofill Variant: Added new tab with digits 1-6 configuration | Sparrow
| 2018-05-31 |  | f | DIGITS 12-15 ACC2: Updated Digit 14 to add Note 4 for Castell locks and included Options "C" & "1" for EGL | Sparrow
| 2018-06-01 |  | g | Rating Plug Matrix: Removed Note 2 for 6000A rating which is now UL/ASNI DIGITS 12-15 ACC2: Added Note 11 to Digit 15 header and ANSI header excluding Mechanical Interlocks and NCT Adapter from AKD20 breakers DIGITS 16-19, IEC GTU: Eliminated column "R" and added note 2: All IEC GF Protection is switchable | Sparrow
| 2018-07-12 |  | h | Digits 1-6 MAIN: Removed strike-through for Digit 3 1250A option on EGG breakers | Sparrow
| 2018-09-20 |  | i | DIGITS 12-15 ACC2: Chaged cell CA5 (digit 15)…update that cell to read EGR MPACT/ME07 DIGITS 16-19, IEC GTU: Inserted EGLR model in column AV; Added Digit 16 ="H" option Digit 17 & 18 = "40" & "50" on rows 67 & 68 DIGITS 12-15 ACC2: Removed Castell lock offering on EGL; Updated Note 4 to "Castell locks for EGG and EGR are FS1" DIGITS 1-6 MAIN: Updated IEC type "S" rating Icm to 105kA; Added type"D" Icm rating of 143kA; Removed type "R" ENV1 option 400-2500A DIGITS 1-6 MAIN: Added type "S" ENV 1 option 400-2500A; Removed type "C" ENV 2 rating 2000-4000A; Added type "D" ENV 2 rating 2000-4000A M-Pact Retrofill Variant: Replaced Digit 2 = "G" Westinghouse with Mpact Retrofill – Mpro TU; Digit 2 = "I" Westinghouse OEM with Mpact Retrofill – GTU M-Pact Retrofill Variant: Replaced Digit 2 = "J" ITE with MPACT Retrofill – Switch, Changed electrical standards to IEC for G, I, and J | Sparrow
| 2019-04-22 |  | j | Retrofill for AKD, and others, i.e. integrally fused breakers. Entellisys Retrofill Update with regards to integrally fused, and fuse truck (OFLO only) related. | Hegarty
Note on F263: Schulz, Gary: Should theis be for Cassettes not Breakers???

## NOMENCLATURE GENERAL
EntelliGuard G, L, and T Families Nomenclature
Breakers/Switches
| Product Line Definition | Product Type | Current Rating |  | Interruption Tier | Construction | Motor Operator | Closing Coils | Shunt Release/Remote Reset/Network Interlock | Undervoltage Release | 2ND Shunt Release/Undervoltage Release | Auxillary Switch/Coil Signaling Contacts | Bell Alarm/Ready to Close/Operations Counter | Key Locks | Mechanical Interlock | Trip Unit Type | Trip Unit Type | UL/ANSI - ZSI Option IEC - Trip Unit Type | UL/ANSI - Advanced Functions IEC - Manual Language | UL/ANSI - Rating Plug IEC - Not Used
| Main Product Construction | [5 empty] | Accessories I |  |  |  |  | Accessories II |  |  |  | Trip Unit/Rating Plug
| G | A | 3 | 2 | M | 1 | J | G | T | 7 | T | 2 | C | K | 1 | L | 3 | Z | 1 | 1
Cassettes
| Product Line Definition | Product Type | Current Rating |  | Interruption Tier | Construction | UL/ANSI - Shutters IEC - Connection Mode | UL/ANSI - Not Used IEC - Delivery Method | UL/ANSI - Not Used IEC - Carriage Position Switches | UL/ANSI - Not Used IEC - Key Locks | UL/ANSI - Not Used IEC - Future | UL/ANSI - Not Used IEC - Future
| Main Product Construction | [5 empty] | Accessories |  |  |  | Future
| G | G | 1 | 3 | H | 2 | U | X | X | X | X | X
Entellysis Family Nomenclature
| Product Line Definition | Product Type | Current Rating |  | Interruption Tier | Frame Size | Motor Operator | Accessory | Future | Future
| Main Product Construction | [5 empty] | Accessories
| E | E | 0 | 8 | S | 1 | M | X | X | X
EntelliGuard R Family Nomenclature
| Product Line Definition | Gear Type | Current Rating |  | Breaker Type | Secondary Disconnect | Motor Operator | Closing Coils | Shunt Release/Remote Reset/Network Interlock | Undervoltage Release | 2ND Shunt Release/Undervoltage Release | Auxillary Switch/Coil Signaling Contacts | Bell Alarm/Ready to Close/Operations Counter | Key Locks | Mechanical Interlock | Trip Unit Type | Trip Unit Type | UL/ANSI - ZSI Option IEC - Trip Unit Type | UL/ANSI - Advanced Functions IEC - Manual Language | UL/ANSI - Rating Plug IEC - Not Used
| Main Product Construction | [5 empty] | Accessories I |  |  |  |  | Accessories II |  |  |  | Trip Unit/Rating Plug
| R | 3 | 0 | 8 | J | 2 | J | G | T | 7 | T | 2 | C | K | 1 | L | 3 | Z | 1 | 1

## DIGITS 1-6 MAIN
EntelliGuard G, L, and T Families Breaker/Switch Nomenclature (1-6)
| DIGIT 1 |  | DIGIT 2 | [6 empty] | DIGITS 3, 4 | [11 empty] | DIGIT 5 | [136 empty] | DIGIT 6 | [6 empty] | Continue…
| PRODUCT LINE DEFINITION |  | PRODUCT TYPE | [6 empty] | CURRENT RATING | [11 empty] | INTERRUPTION TIER (kA) and Frame Size | [136 empty] | CONSTRUCTION
| Character | Description | Character | Description | EntelliGuard G |  |  | EGL | EGT | Character | Description | Breakers |  |  |  |  | Non-Auto CB/Switch |  |  |  |  | EntelliGuard G | [104 empty] | EntelliGuard L | [19 empty] | EntelliGuard T | [11 empty] | Character | Description | EntelliGuard G |  |  | EGL | EGT
[5 empty] | UL | ANSI | IEC | IEC | IEC |  |  | EntelliGuard G |  |  | EGL | EGT | EntelliGuard G |  |  | EGL | EGT | UL489 | [26 empty] | ANSI C37.13/UL1066 | [23 empty] | IEC | [87 empty] | UL | ANSI | IEC
| 1 |  | 1 | [8 empty] | UL | ANSI | IEC |  |  | UL | ANSI | IEC |  |  | Character | Interruptions Ratings |  |  |  |  | Envelope Size by Rated Current | [20 empty] | Character | Interruption Ratings |  |  |  |  | Envelope Size by Rated Current | [17 empty] | Character | Interruption Ratings | [10 empty] | Envelope Size by Rated Current | [73 empty] | 1 | OEM Drawout - 3 Pole | Yes | Yes | Yes | Yes | Yes
| 2 |  | 2 | CF2KA (future) | [5 empty] | 4 | 400A | Yes | Yes | Yes | Yes | Yes |  |  | Yes | Yes | Yes |  | 240V | 480V | 600V | 1/2s W/S | Close & Latch / Switch AIC Rating | Breaker | [11 empty] | Non-Auto CB/Switch | [9 empty] | 254V | 508V | 635V | 1/2s W/S | Close & Latch / Switch AIC Rating | Breaker | [9 empty] | Non-Auto CB/Switch | [8 empty] | Icm (kA) peak Isolator | Icm (kA) peak Breaker/ Switch w/MCR | Icu (kA) @ 230, 240, 400, 415, 440Vac | Icu (kA) @ 500Vac | Icu (kA) @ 690Vac | Icu (kA) @ 1000Vac [4] | Ics (kA) % of Icu | Icw (kA) @ 230-500V | Icw (kA) @ 690V | Icw (kA) @ 1000Vac [4] | Icw (kA) @ 1000/1500 Vdc | Breaker | [13 empty] | Non-Auto CB/Switch | [13 empty] | Non-Auto CB/Switch w/MCR | [13 empty] | Breaker | [9 empty] | Non-Auto CB/Switch | [9 empty] | Breaker | [5 empty] | Non-Auto CB/Switch | [5 empty] | 2 | OEM Drawout - 4 Pole, right | Yes | Yes | Yes[2] | Yes | Yes
| 3 |  | 3 | 2000A MCCB (future) | [5 empty] | 6 | 600A | Yes | [15 empty] | Type GB, GU [1] | [11 empty] | Type GD, GS [1],[8] | [14 empty] | Type GA, GN[1] | [9 empty] | Type GC, GM[1],[8] | [19 empty] | Type GG | [11 empty] | Type GH[6] |  | Type GJ | [11 empty] | Type GK[6] |  | Type GW | [11 empty] | Type GZ[6] |  | Type LG or LI | [9 empty] | Type LJ | [9 empty] | Type GT | [5 empty] | Type G7 | [5 empty] | 3 | OEM Drawout - 4 Pole, left | Yes | Yes | Yes | Yes | Yes
| 4 |  | 4 | NF4KA (future) | [5 empty] | 7 | 630A |  |  | Yes | Yes | Yes |  |  | Yes | Yes | Yes | [6 empty] | 400A | 600A | 800A | 1000A | 1200A | 1600A | 2000A | 2500A | 3000A | 4000A | 5000A | 6000A | 800A | 1200A | 1600A | 2000A | 2500A | 3000A | 4000A | 5000A | 6000A | [6 empty] | 400A | 800A | 1200A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 6000A | 800A | 1200A | 1600A | 2000A | 3200A | 4000A | 5000A | 6000A | [12 empty] | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 6400A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 6400A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 6400A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 4 | OEM Stationary - 3 Pole | Yes | Yes | Yes | Yes | Yes
| 5 |  | 5 | [6 empty] | 8 | 800A | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [137 empty] | 5 | OEM Stationary - 4 Pole, right | Yes | Yes | Yes[2] | Yes | Yes
| 6 |  | 6 | [6 empty] | 10 | 1000A | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes | Yes | [137 empty] | 6 | OEM Stationary - 4 Pole, left | Yes | Yes | Yes | Yes | Yes
| 7 |  | 7 | EntelliGuard T (EGT) Non-Auto CB/Switch [2] |  |  |  |  | Yes | 12 | 1200A | Yes | Yes |  |  |  | Yes | Yes |  |  |  | R | [26 empty] | R | [23 empty] | R[13] | 75 | 105 | 50 | 50 | 42 |  | 100% | 42 | 42 | [54 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | T | T | T | T | T | T | T | T | T | T | T | T | 7
| 8 |  | 8 | EntelliGuard T with MCR[2] - Reserved for FUTURE | [5 empty] | 13 | 1250A |  |  | Yes | Yes | Yes |  |  | Yes | Yes | Yes | S[7] | 65 | 65 | 50 | 42 | 42 | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | [7 empty] | S[7] | 65 | 65 | 50 | 50 | 42 | 1 | 1 | 1 | [7 empty] | 1 | 1 | [6 empty] | S | 88.2 | 105 | 50 | 50 | 40 |  | 100% | 50 | 50 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [20 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [14 empty] | 8
| 9 |  | 9 | [6 empty] | 16 | 1600A | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | C | [26 empty] | C | [23 empty] | C | 105 | 105 | 50 | 50 | 40 |  | 100% | 50 | 50 | [50 empty] | 2 | 2 | 2 | 2 | [6 empty] | 2 | 2 | 2 | 2 | [12 empty] | 9
| 0 |  | 0 | [6 empty] | 20 | 2000A | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes |  | K | [26 empty] | K | [23 empty] | K |  | 143 | 65 | 55 | 50 |  | 77/91/80% [11] | 50 | 42 | [64 empty] | T | T | T | T | T | T | [6 empty] | 0
| A | AEG Branded EntelliGuard G (ME10) | A | ANSI/UL1066 CB - F1 SSD, F2, F2.5, & F3 TSD |  | Yes |  |  |  | 25 | 2500A | Yes | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | F | [26 empty] | F | [23 empty] | F |  | 143 | 85 | 65 | 65 | 35 | 100% | 65/50[14] | 65/50[14] | 35 | [8 empty] | 1 | [27 empty] | 1 | [38 empty] | A | GE Wind Stationary - 3 Pole [4] |  | Yes
| B |  | B | UL489 CB - F1 SSD, F2, F2.5, & F3 TSD | Yes |  |  |  |  | 30 | 3000A | Yes |  |  |  |  | Yes |  |  |  |  | N | 65 | 65 | 65 | 42 | 42 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 |  |  |  | 1 | 1 | 1 | 1 | [5 empty] | N | 65 | 65 | 65 | 65 | 42/65[2] | 1 | 1 | 1 | 1 | 1 | 2 | 2 |  |  |  | 1 |  | 1 | 1 |  |  |  |  | N | 143 | 143 | 65 | 65 | 50/40[15] |  | 100% | 65 | 65 |  | 50 (18) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 |  |  | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [24 empty] | B | GE Wind Stationary - 4 Pole, left [4] |  | Yes
| C |  | C | ANSI/UL1066 Non-Auto CB/Switch - F1 SSD, F2, F2.5, & F3 TSD (ANSI/UL) |  | Yes |  |  |  | 32 | 3200A |  | Yes | Yes | Yes |  |  | Yes | Yes | Yes |  | D | [26 empty] | D | [23 empty] | D | 143 | 143 | 65 | 65 | 40 |  | 100% | 65 | 65 | [50 empty] | 2 | 2 | 2 | 2 | [6 empty] | 2 | 2 | 2 | 2 | [12 empty] | C | GE Wind Stationary - 4 Pole, right [4] |  | Yes
| D |  | D | UL489 Non-Auto CB/Switch - F1 SSD, F2, F2.5, & F3 TSD | Yes |  |  |  |  | 40 | 4000A | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes |  | H | 85 | 85 | 65 | 50 | 42/65[2] | 1 | 1 | 1 | 1 | 1 | 1[10] | 1 | 2 | 2 | [12 empty] | H | 85 | 85 | 65 | 65 | 42 | 1 | 1 | 1 | 1[10] | 1 | [13 empty] | H |  | 187 | 85 | 65/85[2] | 65/85[2] | 35[12] | 100% | 65/85[2] | 65/85[2] | 35[12] |  | 1 | 1 | 1 | 1 | 1 | 1[10] | 1 | 2 | 2 | 2 |  |  | 2 | 2 | [26 empty] | 2 | 2 | [32 empty] | D | GE Drawout - 3 Pole |  | Yes
| E | Entellisys Breaker [1] | E | Entellisys CB [1] |  | Yes |  |  |  | 50 | 5000A | Yes | Yes | Yes |  |  | Yes | Yes | Yes |  |  | P[7] | 100 | 100 | 65 | 50 | 42 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [14 empty] | P[7] | 100 | 100 | 65 | 65 | 42 | 1 | 1 | 1 | 1 | 1 | [13 empty] | P | [85 empty] | E
| F |  | F | UL977 Fused Non-Auto CB/Switch (future) | [5 empty] | 60 | 6000A | Yes | Yes |  |  |  | Yes | Yes |  |  |  | E | [26 empty] | E | 85 | 85 | 85 | 85 | 65 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3[19] | 3[19] | [9 empty] | E |  | 187 | 85 | 85 | 85 |  | 100% | 85 | 85 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [67 empty] | F | GE Stationary - 3 Pole | Yes
| G | EntelliGuard G Breaker & Switch | G | IEC CB |  |  | Yes | Yes |  | 64 | 6400A |  |  | Yes |  |  |  |  | Yes |  |  | M | 100 | 100 | 100 | 65 | 65 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | M | 100 | 100 | 100 | 85 | 65/100[3] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3[16] | 2 |  | 2 | 2 | 2 |  |  |  | M | 187 | 220 | 100 | 100 | 100 | 50[9] | 100% | 85/100[3] | 85/100[3] | 50[4] |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | [14 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [36 empty] | G
| H |  | H | IEC 100% Rated [3] |  |  | Yes | [14 empty] | B | 100 | 100 | 100 | 100 | 100 | [17 empty] | 3 | 3 | 3 | 3 | B | 100 | 100 | 100 | 100 | 100 | [6 empty] | 3 | 3 | 3 | 3[16] |  |  |  |  | 3 | 3 | 3 | 3[16] | B | [85 empty] | H
| I |  | I | EGL w/comm (EGL) |  |  |  | Yes |  | Notes: | See Digit 5 for current ratings by interruption tier and frame size | [10 empty] | G | [26 empty] | G | [23 empty] | G |  | 220 | 100 | 100 | 100 |  | 100% | 100 | 100 | [10 empty] | 3 | 3 | [64 empty] | I
| J |  | J | IEC Non-Auto CB/Switch |  |  | Yes | Yes |  |  | [1] Future | [10 empty] | L | 100 | 100 | 100 | 85 | 100 | [8 empty] | 3 | 3 | 3 | 3 | [9 empty] | L | 150 | 150 | 100 | 100 | 100 | [6 empty] | 3 | 3 | 3 | 3[16] | [8 empty] | L | 220 | 330 | 150 | 150 | 150 |  | 100% | 100 | 100 | [10 empty] | 3 | 3 | 3 | 3 | [10 empty] | 3 | 3 | 3 | 3 | [48 empty] | J
| K |  | K | IEC Non-Auto CB/Switch 100% Rated [3] |  |  | Yes | [14 empty] | U[7] | 130 | 100 | 100 | 85 | 85 |  |  | 2.5[7] |  | 2.5[7] | 2.5[7] | 2.5[7] | 2.5[7] | 2.5[7] | 2.5[7] | [5 empty] | 2.5[7] |  | 2.5[7] | 2.5[7] |  |  | U[7] | 130 | 100 | 100 | 100 | 85 |  | 2.5[7] | 2.5[7] | 2.5[7] | 2.5[7] | 2.5[7] | 2.5[7] | 2.5[7] | [5 empty] | 2.5[7] | 2.5[7] | 2.5[7] |  |  | U | [85 empty] | K
| L | EntelliGuard L Breaker & Switch (EGL) [2] | L | UL489B DC Non-Auto CB/Switch [1] | Yes | [16 empty] | V | 200 | 200 | 100 | 30 | 57.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [14 empty] | V | 200 | 200 | 100 | 30 | 57.5 | 2 | 2 | 2 | 2 | 2 | [13 empty] | V | [85 empty] | L | GE Drawout - 4 Pole, left (future)
| M | EntelliGuard Breaker & Switch w/ AEG Label (ME09) | M | ANSI/UL1066 Non-Auto CB/Switch - F1 Only, TSD |  | Yes | [15 empty] | W | 200 | 200 | 100 | 100 | 100 | [8 empty] | 3[6] | 3[6] | 3[6] | 3[6] | [9 empty] | W | 200 | 200 | 100 | 100 | 100 | [6 empty] | 3[6] | 3[6] | 3[6] | 3[16] | [8 empty] | W | [85 empty] | M
| N |  | N | ANSI/UL1066 CB - F1 Only, TSD |  | Yes | [15 empty] | Notes: | [50 empty] | T[17] | [10 empty] | 50 | [16 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [50 empty] | N
| O |  | O | [19 empty] | [1] Env. 1 Only for GN, GU, GM, GS | [135 empty] | O
| P |  | P | GE Wind 1400V Breaker [4] | Yes | Yes | Yes | [15 empty] | [2] Env. 1/Env. 2, respectively | [135 empty] | P
| Q |  | Q | [19 empty] | [3] Env. 2/Env. 3, respectively | [135 empty] | Q
| R | EntelliGuard R Retrofill [1] | R | AEG branded retrofill (future) | [18 empty] | [4] For use at 1000Vac, phase separators are required | [135 empty] | R | GE Drawout - 4 Pole, right (future)
| S |  | S | UL489 Non-Auto CB/Switch - F1 Only TSD | Yes | [17 empty] | [5] Internally tested only. Not IEC certified | [135 empty] | S | GE Drawout - 3 Pole Single Cluster [1] |  | Yes
| T |  | T | EntelliGuard T (EGT) CB [2] |  |  |  |  | Yes | [13 empty] | [6] Drawout only | [135 empty] | T
| U |  | U | UL489 CB - F1 Only, TSD | Yes | [17 empty] | [7] 3 Pole only | [135 empty] | U
| V |  | V | [19 empty] | [8] Non-Auto CB/Switches take close and latch ratings as interruption ratings | [135 empty] | V | GE Stationary - 4 Pole, right | Yes
| W |  | W | IEC Non-Auto CB/Switch w/MCR |  |  | Yes | [15 empty] | [9] Env. 2 Only | [135 empty] | W | GE Stationary - 4 Pole, left | Yes
| X |  | X | [19 empty] | [10] GY16HS and GP16HS rated @ 13kAIC | [135 empty] | X | OEM Stationary - 3 Pole, No Rear Terminations | Yes | Yes | Yes
| Y |  | Y | GE Wind 1400V Switch [5] | Yes | Yes | Yes | [15 empty] | [11] Values for 440V/500V/690V | [135 empty] | Y | OEM Stationary - 4 Pole, Right, No Rear Terminations | Yes | Yes | Yes
| Z |  | Z | IEC Non-Auto CB/Switch 100% Rated w/MCR [3] |  |  | Yes | [15 empty] | [12] Envelope 1 Only | [135 empty] | Z | OEM Stationary - 4 Pole, Left, No Rear Terminations | Yes | Yes | Yes
| Notes: |  | Notes: | [19 empty] | [13] EGL Switches have Icu = 42kA only | [135 empty] | Notes:
|  | [1] AK_AKR_WP See Variant Tab |  | General: This character affects the SD assignment. Refer to 10101883P1 and 11112222P1 | [18 empty] | [14] 1 second/3 second | [136 empty] | General: This character affects the SD assignment. Refer to 10101883P1 and 11112222P1
|  | M-Pact See Variant Tab |  | [1] See Variant | [18 empty] | [15] EGG/EGL ratings respectively | [136 empty] | [1] F2, 2000A and less, interruption tiers E and M. Available for GE Burlington Only
|  | [2] Refer to EGL columns for availability |  | [2] Specific Conditions apply only available when noted in "EGT" column. Only available for Digit 1 = "G" | [18 empty] | [16] For fan cooled AKD20 switchgear only | [136 empty] | [2] Not available for digit 5 = "F"
|  |  |  | [3] Drawout Only | [18 empty] | [17] 1500 VDC and 4pole configurations only. Digit 6 options "3" or "6". | [136 empty] | [3] Not available for sale in Europe
[18] 1000 VDC only available for GJ25Nx and GJ32Nx switches
|  |  |  | [4] Only available as GP16HS | [18 empty] | [19] Tier "E" ANSI 4000A & 5000A breakers are restricted to Saudi only | [136 empty] | [4] Available for GE Wind Only
[5] Only available as GY16HS
[6] Planned Q4 2015
SSD - Side-mounted Secondary Disconnect
TSD - Top-mounted Seconddary Disconnect
R
SϮϮϮ
C
K
N
D
H
PϮϮϮ
E
M
B
G
L
U
Y
W
A
F
I
J
O
Q
[22 empty] | T | 200k F2 UL
[22 empty] | V | 200k F2 ANSI
X
Z
Future
FUTURE
FUTURE

## Cassette
EntelliGuard G, L, and T Families Cassette Nomenclature
IEC Variant
| DIGIT 1 |  | DIGIT 2 | [6 empty] | DIGITS 3, 4 | [11 empty] | DIGIT 5 | [133 empty] | DIGIT 6 | [7 empty] | DIGIT 7 | [5 empty] | DIGIT 8 |  |  |  |  | DIGIT 9 |  |  |  |  | DIGIT 10,11 |  | DIGIT 12 |  | Complete IEC Cat #
| PRODUCT LINE DEFINITION |  | PRODUCT TYPE | [6 empty] | CURRENT RATING | [11 empty] | INTERRUPTION TIER (kA) and Frame Size | [133 empty] | CONSTRUCTION | [7 empty] | CONNECTION MODE | [5 empty] | POSITION SWITCHES |  |  |  |  | KEY LOCKS |  |  |  |  | FUTURE USE |  | DELIVERY MODE
| Character | Description | Character | Description | EntelliGuard G |  |  | EGL | EGT | Character | Description | Breakers |  |  |  |  | Non-Auto CB/Switch |  |  |  |  | EntelliGuard G | [101 empty] | EntelliGuard L | [19 empty] | EntelliGuard T | [11 empty] | Character | Description | EntelliGuard G |  |  | EGL | EGT |  | Character | Description | EGG | EGL | EGT |  | Character | Description | EGG | EGL | EGT | Character | Description | EGG | EGL | EGT | Character | Description | Character | Description
[5 empty] | UL | ANSI | IEC |  |  |  |  | EntelliGuard G |  |  | EGL | EGT | EntelliGuard G |  |  | EGL | EGT | UL489 | [26 empty] | UL1066/ANSI C37.13 | [22 empty] | IEC | [85 empty] | UL | ANSI | IEC | [5 empty] | IEC | [5 empty] | IEC |  |  |  |  | IEC
| 1 |  | 1 | [8 empty] | UL | ANSI | IEC |  |  | UL | ANSI | IEC |  |  | Character | Interruptions Ratings |  |  |  |  | Envelope Size by Amperage | [20 empty] | Character | Interruption Ratings |  |  |  |  | Envelope Size by Amperage | [15 empty] | Character | Interruption Ratings | [9 empty] | Envelope Size by Amperage | [73 empty] | 2 | OEM Drawout - 3 Pole | Yes | Yes | Yes | Yes | Yes |  | U | Rear Universal, T Stubs Rotatable for Horizontal or Vertical Buss | Yes | Yes | Yes |  | 2 | Set of 1 NO and 1NC contacts per Position | Yes | Yes | Yes | X | No Lock Prevision mounted | Yes | Yes | Yes | XX |  | M | Mounted with Breaker
| 2 |  | 2 | [6 empty] | 4 | 400A | [11 empty] | 240V | 480V | 600V | 1/2s W/S | Close & Latch / Switch AIC Rating | Breaker | [11 empty] | Non Automatic CB (Switch) | [9 empty] | 254V | 508V | 635V | 1/2s W/S | Close & Latch / Switch AIC Rating | Breaker | [8 empty] | Non Automatic CB (Switch) | [7 empty] | Icm (kA) peak Isolator | Icm (kA) peak Breaker/ Switch w/MCR | Icu (kA) @ 230, 240, 400, 415, 440Vac | Icu (kA) @ 500Vac | Icu (kA) @ 690Vac | Icu (kA) @ 1000Vac | Ics (kA) % of Icu | Icw (kA) @ 230-500V | Icw (kA) @ 690V | Icw (kA) @ 1000Vac | Breaker | [13 empty] | Non-Auto CB(Switch) (GJ, GK Switch) | [13 empty] | Non-Auto CB(Switch) w/MCR (Type GW, GZ Switch) | [13 empty] | Breaker | [9 empty] | Non Automatic CB (LJ Switch) | [9 empty] | Breaker | [5 empty] | Non Automatic CB (G7 Switch) | [5 empty] | 5 | OEM Drawout - 4 Pole | Yes | Yes | Yes | Yes | Yes |  | F | Flat Front Access | Yes | Yes | Yes |  | 4 | Set of 2 NO and 2NC contacts per Position | Yes | Yes | Yes | Provision Only | [6 empty] | R | As separate component
| 3 |  | 3 | [6 empty] | 6 | 600A | [16 empty] | Type GB, GU[1] | [11 empty] | Type GD, GS[1] | [14 empty] | Type GA, GN[1] | [8 empty] | Type GC, GM[1] | [17 empty] | Type GG | [11 empty] | Type GH |  | GJ->Use Type GG | [11 empty] | GK->Use Type GH |  | GW->Use Type GG | [11 empty] | GZ->Use Type GH |  | Type LG | [9 empty] | LJ-> UseType LG | [9 empty] | Type GT | [5 empty] | G7-> UseType GT | [5 empty] | X | OEM Drawout - 3 Pole, No Rear Terminations [1] | Yes | Yes |  |  |  |  | H | Rear Horizontal Buss |  | Yes | Yes |  | 5 | Carriage Position Switch - 1 NO/1NC power rated, 1 NO/1NC signal rated | Yes |  | Yes | R | For 1 Ronis Key lock | Yes | Yes | Yes
| 4 |  | 4 | [6 empty] | 7 | 630A | [16 empty] | 400A | 600A | 800A | 1000A | 1200A | 1600A | 2000A | 2500A | 3000A | 4000A | 5000A | 6000A | 800A | 1200A | 1600A | 2000A | 2500A | 3000A | 4000A | 5000A | 6000A | [6 empty] | 400A | 800A | 1200A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 800A | 1200A | 1600A | 2000A | 3200A | 4000A | 5000A | [11 empty] | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 6400A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 6400A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 6400A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 400A | 630A | 800A | 1000A | 1250A | 1600A | Y | OEM Drawout - 4 Pole, No Rear Terminations [1] | Yes | Yes |  |  |  |  | V | Rear Vertical Buss | Yes | Yes | No[1] |  | 7 | Carriage Position Switch - 5 NO/1NC power rated (connect), 1 NO/1NC power rated (test & connect) |  |  |  | S | For 2 Ronis Key locks | Yes
| 5 |  | 5 | [6 empty] | 8 | 800A | Yes | Yes |  |  |  | Yes | Yes | [137 empty] | Notes: | [7 empty] | X | No Rear Terminations | Yes | Yes | Yes |  | X | None | Yes | Yes | Yes | P | For 1 Profalux Key lock | Yes | Yes | Yes
| 6 |  | 6 | [6 empty] | 10 | 1000A | [145 empty] | [1] Only available for Envelope 2 >2000A, Envelope 2.5, or Envelope 3 | [6 empty] | [1] = Not in Catalog and not in Factory Decoder | [10 empty] | Q | For 2 Profalux Key locks | Yes
| 7 |  | 7 | EntelliGuard T (EGT) Switch | [5 empty] | 12 | 1200A | Yes | Yes |  |  |  | Yes | Yes |  |  |  | R | [26 empty] | R | [21 empty] | R | 75 | 105 | 50 | 50 | 42 |  | 100% | 42 | 42 | [82 empty] | UL/ANSI Variant | [11 empty] | T | 1 Ronis key lock shutter interlock | Yes |  | Yes
| 8 |  | 8 | [6 empty] | 13 | 1250A | [10 empty] | S[7] | 65 | 65 | 50 | 42 | 42 |  |  |  |  | 1 | [8 empty] | 1 | [7 empty] | S[7] | 65 | 65 | 50 | 50 | 42 |  |  | 1 | [7 empty] | 1 | [5 empty] | S | 88.2 | 105 | 50 | 50 | 40 |  | 100% | 50 | 50 | [6 empty] | 1 | [13 empty] | 1 | [27 empty] | 1 | [9 empty] | 1 | [29 empty] | Complete UL/ANSI Catalog # | [5 empty] | U | 1 Profalux key lock shutter interlock |  |  | Yes
| 9 |  | 9 | [6 empty] | 16 | 1600A | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | C | [26 empty] | C | [21 empty] | C | 105 | 105 | 50 | 50 | 40 |  | 100% | 50 | 42 | [83 empty] | DIGIT 7 | [10 empty] | Lock Cylinder Mounted [1]
| 0 |  | 0 | [6 empty] | 20 | 2000A | Yes | Yes | Yes | Yes |  | Yes | Yes | Yes | Yes |  | K | [26 empty] | K | [21 empty] | K |  | 143 | 65 | 50 | 42 |  | 100% | 50 | 42 | [68 empty] | T | [5 empty] | T | [8 empty] | SHUTTERS | [10 empty] | G | 1 Ronis Key lock | Yes | Yes | Yes
| A | AEG Branded EntelliGuard G (ME10) [1] | A | ANSI/UL1066 CB - F1 SSD, F2 & F3 TSD |  | Yes |  |  |  | 25 | 2500A |  |  | Yes | Yes |  |  |  | Yes | Yes |  | N | 65 | 65 | 65 | 42 | 42 |  |  | 1 |  |  | 1 | 1 |  | 2 |  |  |  | 1 |  | 1 | 1 | [5 empty] | N | 65 | 65 | 65 | 65 | 42/65[2] |  | 1 |  | 1 | 1 |  | 2 |  |  | 1 |  | 1 | 1 |  |  |  | N | 143 | 143 | 65 | 65 | 50 |  | 100% | 65 | 65 | [49 empty] | 1[11] | 1[12] | [8 empty] | 1[11] | 1[12] | [22 empty] | Character | Description | EGG | [8 empty] | H | 2 Ronis Key locks | Yes
| B |  | B | UL489 CB - F1 SSD, F2 & F3 TSD | Yes |  |  |  |  | 30 | 3000A | Yes |  |  |  |  | Yes |  |  |  |  | D | [26 empty] | D | [21 empty] | D |  | 143 | 65 | 65 | 40 |  | 100% | 65 | 40 | [51 empty] | 2 | 2 | [8 empty] | 2 | 2 | [22 empty] | UL | ANSI | [7 empty] | J | 1 Profalux Key lock | Yes | Yes | Yes
| C |  | C | ANSI/UL1066 Switch - F1 SSD, F2 & F3 TSD |  | Yes |  |  |  | 32 | 3200A |  | Yes | Yes | Yes |  |  | Yes | Yes | Yes |  | H | 85 | 85 | 65 | 50 | 42/65[2] |  |  | 1 |  |  | 1 | 1 |  | 2 | [12 empty] | H | 85 | 85 | 65 | 65 | 42 |  | 1 |  | 1 | 1 | [11 empty] | H |  | 187 | 85 | 65 | 65 | 35 | 100% | 65 | 65 | 35[4] | [5 empty] | 1 | 1 | 1 | [25 empty] | 1 | 1 | [47 empty] | S | Shutter Insalled | Yes | [8 empty] | K | 2 Profalux Key locks | Yes
| D |  | D | UL489 Switch - F1 SSD, F2 & F3 TSD | Yes |  |  |  |  | 40 | 4000A |  |  | Yes | Yes |  |  |  | Yes | Yes |  | F | [26 empty] | F | [21 empty] | F |  | 65 | 85 | 65 | 65 | 35 | 100% | 65/50[14] | 65/50[14] | 35[4] | [7 empty] | 1 | [13 empty] | 1 | [60 empty] | X | None | Yes | [8 empty] | M | 1 Ronis key lock shutter interlock | Yes |  | Yes
| E |  | E | [6 empty] | 50 | 5000A |  | Yes |  |  |  |  | Yes |  |  |  | P[7] | 100 | 100 | 65 | 50 | 42 |  |  | 1 |  |  | 1 | 1 | [14 empty] | P[7] | 100 | 100 | 65 | 65 | 42 |  | 1 |  | 1 | 1 | [11 empty] | P[7] | [103 empty] | N | 1 Profalux key lock shutter interlock |  |  | Yes
| F |  | F | [6 empty] | 60 | 6000A | Yes |  |  |  |  | Yes |  |  |  |  | E | [26 empty] | E | 85 | 85 | 85 | 85 | 65 |  | 2 |  | 2 | 2 |  | 2 | [9 empty] | E |  | 187 | 85 | 85 | 85 |  | 100% | 85 | 85 | [94 empty] | Notes:
| G | EntelliGuard G Breaker & Switch | G | IEC CB |  |  | Yes | Yes |  | 64 | 6400A |  |  | Yes |  |  |  |  | Yes |  |  | M | 100 | 100 | 100 | 65 | 65 |  |  | 2 |  |  | 2 | 2 |  | 2 |  |  | 3 |  |  | 2 | 2 |  | 2 |  |  |  | M | 100 | 100 | 100 | 85 | 65/100[3] |  | 2 |  | 2 | 2 |  | 2 |  | 3 |  |  | 2 | 2 | 2 |  |  | M | 187 | 220 | 100 | 100 | 85 | 50 | 100% | 85 | 85 | 50[4] | [6 empty] | 2 | 2 | 2 | 2 |  |  | 2 | 2 | [12 empty] | 2 | 2 | [6 empty] | 2 | 2 | 2 | 2 |  |  | 2 | 2 | [51 empty] | [1] Lock will have random lock cylinder number. Cannot be coordinated
| H |  | H | IEC 100% Rated |  |  | Yes |  |  | Notes: | [11 empty] | B | 100 | 100 | 100 | 100 | 100 | [17 empty] | 3 |  |  | 3 | B | 100 | 100 | 100 | 100 | 100 | [6 empty] | 3 |  | 3 |  |  |  |  | 3 |  | 3 | B | [87 empty] | 945.6495
| I |  | I | [7 empty] | Cassette current rating will determine maximum current rating of breaker/switch | [10 empty] | G | [26 empty] | G | [21 empty] | G |  | 220 | 100 | 100 | 100 |  | 100% | 100 | 100
| J |  | J | IEC Non-Automatic CB (Switch) | [17 empty] | L | 100 | 100 | 100 | 85 | 100 | [8 empty] | 3 |  |  | 3 | [9 empty] | L | 150 | 150 | 100 | 100 | 100 | [6 empty] | 3 |  | 3 | [7 empty] | L | 220 | 330 | 150 | 150 | 150 |  | 100% | 100 | 100 | [12 empty] | 3 | [13 empty] | 3 | [13 empty] | 3
| K |  | K | IEC Non-Automatic CB (Switch) 100% Rated | [17 empty] | U | 100 | 100 | 100 | 85 | 65 |  |  | 2.5 |  | 2.5 | 2.5 | 2.5 |  | 2.5 | 2.5 | [5 empty] | 2.5 |  | 2.5 | 2.5 |  |  | U | 100 | 100 | 100 | 100 | 65 |  | 2.5 | 2.5 | 2.5 | 2.5 |  | 2.5 | 2.5 |  |  |  |  | 2.5 | 2.5 | 2.5 |  | U
| L | EntelliGuard L Breaker & Switch (EGL) [2] | L | UL489B DC Non Auto CB [1] | Yes | [16 empty] | V | 200 | 200 | 100 | 30 | 57.5 |  |  | 2 |  |  | 2 | 2 |  | 2 | [12 empty] | V | 200 | 200 | 100 | 30 | 57.5 |  | 2 |  | 2 | 2 |  | 2 | [9 empty] | V
| M |  | M | ANSI/UL1066 Switch - F1 Only, TSD |  | Yes | [15 empty] | W | 200 | 200 | 100 | 85 | 100 | [8 empty] | 3 |  |  | 3 | [9 empty] | W | 200 | 200 | 100 | 100 | 100 | [6 empty] | 3 |  | 3 | [7 empty] | W
| N |  | N | ANSI/UL1066 CB - F1 Only, TSD |  | Yes | [15 empty] | Notes:
| O |  | O | [19 empty] | [1] Env. 1 Only for GN, GU, GM, GS
| P |  | P | GE Wind 1600V Breaker | Yes | [17 empty] | [2] Env. 1/Env. 2, respectively | [134 empty] | 160 |  |  |  | 945649.5
| Q |  | Q | [19 empty] | [3] Env. 2/Env. 3, respectively | [134 empty] | 210 |  |  |  | 78.8041
| R | EntelliGuard R Retrofill (See Variant) | R | [19 empty] | [4] For use at 1000Vac, phase seperators are required | [134 empty] | 65 |  |  |  | 435
| S |  | S | UL489 Switch - F1 Only TSD | Yes | [17 empty] | [5] Internally tested only. Not IEC certified | [134 empty] | 435 |  |  |  | 5.52
| T |  | T | EntelliGuard T (EGT) CB [2] |  |  |  |  | Yes | [13 empty] | [6] Drawout only
| U |  | U | UL489 CB - F1 Only, TSD | Yes | [17 empty] | [7] 3 Pole only
| V |  | V | [19 empty] | [8] Non-Auto CB/Switches take close and latch ratings as interruption ratings | [134 empty] | 2020 |  |  |  | 8620924.5
| W |  | W | [19 empty] | [9] Env. 2 Only
| X |  | X | [19 empty] | [10] GY16HS and GP16HS rated @ 13kAIC
| Y |  | Y | [19 empty] | [11] Horizontal Rear Connected Only
| Z |  | Z | [19 empty] | [12] Standard and Universal Connected Only
| Notes: |  | Notes: | [19 empty] | [13] EGL Switches have Icu = 42kA only
|  | [1] See Variant |  | [1] See Variant | [18 empty] | [14] 1 second/3 second
|  | [2] Specific Conditions apply only when noted. Takes IEC Descriptions |  | [2] Specific Conditions apply only available when noted. | [18 empty] | [15] EGG/EGL ratings respectively
SSD - Side-mounted Secondary Disconnect
TSD - Top-mounted Seconddary Disconnect
R
SϮϮϮ
C
K
N
D
H
PϮϮϮ
E
M
B
G
L
U
Y
W
A
F
I
J
O
Q
[22 empty] | T | 200k F2 UL
[22 empty] | V | 200k F2 ANSI
X
Z

## DIGITS 7-11 ACC1
EntelliGuard G, L, T, and R Families Breaker/Switch Nomenclature (7-11)
Back
| DIGIT 7 | [6 empty] | DIGIT 8 (Third slot) | [6 empty] | DIGIT 9 (Left Slot) | [8 empty] | DIGIT 10 (Second slot) | [8 empty] | DIGIT 11 | [8 empty] | Continue…
| MOTOR OPERATOR | [6 empty] | CLOSING COILS | [6 empty] | SHUNT RELEASE / REMOTE RESET / NETWORK INTERLOCK | [8 empty] | UNDERVOLTAGE RELEASE | [8 empty] | 2nd SHUNT RELEASE/UNDERVOLTAGE RELEASE/OFLO
| Character | Description | EGG | EGG, EGR |  | EGL | EGT | Character | Description (Approvals) | EGG | EGG, EGR |  | EGL | EGT | Character | Description | EGG | EGG, EGR | EGG | EGL | EGT | EGR ME07 S10/20 | EGR ME07 S30/40 | Character | Description | EGG | EGG, EGR | EGG | EGL | EGT | EGR ME07 S10/20 | EGR ME07 S30/40 | Character | Description | EGG | EGG, EGR | EGG | EGL | EGT | EGR ME07 S10/20 | EGR ME07 S30/40
|  |  | UL | ANSI | IEC |  |  |  |  | UL | ANSI | IEC |  |  |  |  | UL | ANSI | IEC | [6 empty] | UL | ANSI | IEC | [6 empty] | UL | ANSI | IEC
| A | 24-30 Vdc (IEC) / 24 Vdc (UL/ANSI) | Yes | Yes | Yes | Yes | Yes | Closing Coil | [6 empty] | SHUNT RELEASE | [8 empty] | 1 | 24 Vdc | Yes | Yes | Yes | Yes | Yes | Yes | Yes | SHUNT RELEASE
| B | 48 Vdc | Yes | Yes | Yes |  | Yes | A | 24 Vdc (UL/ANSI) | Yes | Yes | Yes | Yes | Yes | A | 24 Vdc |  |  | Yes | Yes | Yes | Yes | Yes | 2 | 30 Vdc | Yes | Yes | [5 empty] | A | 24 Vdc |  |  | Yes |  |  |  | Yes
| C | 60 Vdc | Yes | Yes | Yes |  | Yes | B | 30 Vdc (UL/ANSI) | Yes | Yes |  |  |  | B | 30 Vdc |  |  | Yes |  | Yes | Yes | Yes | 3 | 48 Vac/dc | Yes | Yes | Yes | Yes | Yes | Yes | Yes | B | 30 Vdc |  |  | Yes |  |  |  | Yes
| D | 72 Vdc | [5 empty] | C | 48 Vac/dc (UL/ANSI) | Yes | Yes | Yes |  | Yes | C | 48 Vac/dc |  |  | Yes | Yes | Yes | Yes | Yes | 4 | 60-72Vdc (IEC) / 60 Vdc (UL/ANSI) | Yes | Yes | Yes |  | Yes | Yes | Yes | C | 48 Vac/dc |  |  | Yes |  |  |  | Yes
| E | 110-130 Vdc | Yes | Yes | Yes | Yes | Yes | D | 60-72 Vdc (UL/ANSI) | Yes | Yes | Yes |  | Yes | D | 60-72 Vdc |  |  | Yes |  | Yes | Yes | Yes | 5 | 110-130 Vac, 120Vdc (IEC) / 120 Vac/dc (UL/ANSI) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | D | 60-72 Vdc |  |  | Yes |  |  |  | Yes
| 6 | 220 Vdc |  |  | Yes | Yes | Yes | E | 110-130 Vac/dc (IEC/UL/ANSI) | Yes | Yes | Yes | Yes | Yes | E | 110-130 Vac/dc |  |  | Yes | Yes | Yes | Yes | Yes | 6 | 208 Vac | Yes | Yes | [5 empty] | E | 110-130 Vac/dc |  |  | Yes |  |  |  | Yes
| F | 250 Vdc | Yes | Yes | Yes |  | Yes | F | 208 Vac (UL/ANSI) | Yes | Yes |  |  |  | F | 208 Vac | [7 empty] | 7 | 220-240 Vac/dc (IEC) / 240 Vac/dc (UL/ANSI) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | F | 208 Vac
| G | 48 Vac | Yes | Yes | Yes |  | Yes | G | 220-240 Vac/dc (IEC/UL/ANSI) | Yes | Yes | Yes | Yes | Yes | G | 220-240 Vac/dc |  |  | Yes | Yes | Yes | Yes | Yes | 8 | 250 Vdc, 277 Vac (IEC) / 277 Vac (UL/ANSI) | Yes | Yes | Yes |  | Yes | Yes | Yes | G | 220-240 Vac/dc |  |  | Yes |  |  |  | Yes
| H | 110-130 Vac (IEC) / 120Vac (UL/ANSI) | Yes | Yes | Yes | Yes | Yes | H | 250 Vdc (Non-UL) / 250-277 Vac (UL/ANSI) | Yes | Yes | Yes |  | Yes | H | 250 Vdc, 250-277 Vac |  |  | Yes |  | Yes | Yes | Yes | 9 | 220-240 Vac/dc 60msec response |  |  | Yes |  | Yes | Yes | Yes | H | 250 Vdc, 250-277 Vac |  |  | Yes |  |  |  | Yes
| J | 220-240 Vac (IEC) / 240 Vac (UL/ANSI) | Yes | Yes | Yes | Yes | Yes | K | 380-415 Vac |  |  | Yes |  | Yes | K | 380-415 Vac |  |  | Yes | Yes | Yes | Yes | Yes | W | 380-415 Vac |  |  | Yes | Yes | Yes | Yes | Yes | K | 380-415 Vac |  |  | Yes |  |  |  | Yes
| K | 277 Vac | Yes | Yes |  |  |  | L | 440 Vac |  |  | Yes |  | Yes | L | 440 Vac |  |  | Yes |  | Yes | Yes | Yes | Y | 440 Vac |  |  | Yes |  | Yes | Yes | Yes | L | 440 Vac |  |  | Yes |  |  |  | Yes
| M | 380-415 Vac |  |  | Yes |  | Yes | X | None | Yes | Yes | Yes | Yes | Yes | M | 24 Vdc | Yes | Yes | [5 empty] | X | None | Yes | Yes | Yes | Yes | Yes | Yes | Yes | M | 24 Vdc | Yes | Yes
| N | 440 Vac |  |  | Yes |  | Yes | Command Closing Coils [1] | [6 empty] | P | 48 Vac/dc | Yes | Yes | [14 empty] | P | 48 Vac/dc | Yes | Yes
| X | None | Yes | Yes | Yes | Yes | Yes | M | 24 Vdc (UL/ANSI) | Yes | Yes | Yes |  | Yes | Q | 72 Vdc | Yes | Yes | [5 empty] | DIGIT 10[1] | [8 empty] | Q | 72 Vdc | Yes | Yes
[8 empty] | N | 30 Vdc (UL/ANSI) | Yes | Yes |  |  |  | R | 120 Vac/dc | Yes | Yes | [5 empty] | NETWORK INTERLOCK (Uses left and Second slot) | [8 empty] | R | 120 Vac/dc | Yes | Yes
[8 empty] | P | 48 Vac/dc (UL/ANSI) | Yes | Yes | Yes |  | Yes | S | 208 Vac | Yes | Yes | [5 empty] | Character | Description | EGG | EGG, EGR | EGG | EGL | EGT | EGR ME07 S10/20 | EGR ME07 S30/40 | S | 208 Vac | Yes | Yes
[8 empty] | Q | 60-72 Vdc (UL/ANSI) | Yes | Yes | Yes |  | Yes | T | 240 Vac | Yes | Yes | [7 empty] | UL | ANSI | IEC |  |  |  |  | T | 240 Vac | Yes | Yes
[8 empty] | R | 110-130 Vac/dc (IEC/UL/ANSI) | Yes | Yes | Yes |  | Yes | V | 250 Vdc | Yes | Yes | [5 empty] | 1 | 24 Vdc | [7 empty] | V | 250 Vdc | Yes | Yes
[8 empty] | S | 208 Vac (UL/ANSI) | Yes | Yes |  |  |  | X | None | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2 | 30 Vdc | [7 empty] | X | None | Yes | Yes | Yes | Yes | Yes | Yes | Yes
[8 empty] | T | 220-240 Vac/dc (IEC/UL/ANSI) | Yes | Yes | Yes |  | Yes | REMOTE RESET[1] | [8 empty] | 3 | 48 Vac/dc | [7 empty] | UNDERVOLTAGE RELEASE
[8 empty] | U | 250 Vdc (Non-UL) / 250-277 Vac (UL/ANSI) | Yes | Yes | Yes |  | Yes | Z | 24 Vdc |  |  | Yes |  |  |  | Yes | 4 | 60 Vdc | [7 empty] | 1 | 24 Vdc | Yes | Yes | Yes |  |  |  | Yes
[8 empty] | W | 380-415 Vac |  |  | Yes |  | Yes | 3 | 48 Vac/dc | [7 empty] | 5 | 110-130 Vac/dc (IEC) / 120 Vac/dc (UL/ANSI) | Yes | Yes | Yes |  |  |  | Yes | 2 | 30 Vdc | Yes | Yes
[8 empty] | Y | 440 Vac |  |  | Yes |  | Yes | 4 | 60-72 Vdc | [7 empty] | 6 | 208 Vac | [7 empty] | 3 | 48 Vac/dc | Yes | Yes | Yes |  |  |  | Yes
[8 empty] | X | None | Yes | Yes | Yes |  | Yes | 5 | 110-130 Vac/dc |  |  | Yes |  |  |  | Yes | 7 | 220-240 Vac/dc (IEC) / 240 Vac/dc (UL/ANSI) |  |  | Yes |  |  |  | Yes | 4 | 60-72Vdc (IEC) / 60 Vdc (UL/ANSI) | Yes | Yes | Yes |  |  |  | Yes
[8 empty] | Notes | [6 empty] | 7 | 220-240 Vac/dc |  |  | Yes |  |  |  | Yes | 8 | 250 Vdc, 250-277 Vac (IEC) / 277 Vac (UL/ANSI) | [7 empty] | 5 | 110-130 Vac, 120Vdc (IEC) / 120 Vac/dc (UL/ANSI) | Yes | Yes | Yes |  |  |  | Yes
[8 empty] | 1) UL/ANSI GCCC includes Electrical Close Switch GECP | [6 empty] | 8 | 250 Vdc, 250-277 Vac | [7 empty] | 9 | 220-240 Vac/dc 60msec response | [7 empty] | 6 | 208 Vac | Yes | Yes
[15 empty] | W | 380-415 Vac | [7 empty] | W | 380-415 Vac | [7 empty] | 7 | 220-240 Vac/dc (IEC) / 240 Vac/dc (UL/ANSI) | Yes | Yes | Yes |  |  |  | Yes
[15 empty] | Y | 440 Vac | [7 empty] | Y | 440 Vac | [7 empty] | 8 | 250 Vdc, 277 Vac (IEC) / 277 Vac (UL/ANSI) | Yes | Yes | Yes |  |  |  | Yes
[15 empty] | NETWORK INTERLOCK (Uses left and Second slot) | [8 empty] | Z | Reserved for internal purpose (2) | [7 empty] | 9 | 220-240 Vac/dc 60msec response |  |  | Yes |  |  |  | Yes
[15 empty] | 1 | System Installed | Yes | Yes | Yes |  |  |  | Yes | Notes: | [1] Only applicable when Digit 9 = "1" | [7 empty] | W | 380-415 Vac |  |  | Yes |  |  |  | Yes
[15 empty] | SHUNT RELEASE - NON-CONTINUOUSLY RATED | [9 empty] | [2] To test single slot Network interlock in Entellisys Retrofill | [7 empty] | Y | 440 Vac |  |  | Yes |  |  |  | Yes
[15 empty] | F | 24Vdc | Yes | Yes | Yes |  | Yes | Yes | Yes | [9 empty] | X | None | Yes | Yes | Yes | Yes | Yes | Yes | Yes
[15 empty] | J | 120 Vac/dc | Yes | Yes | Yes |  | Yes | Yes | Yes | DIGIT 10 (Per special requirements of ABB Rotterdam) | [8 empty] | SHUNT RELEASE - NON-CONTINUOUSLY RATED
[15 empty] | U | 240 Vac/dc | Yes | Yes | Yes |  | Yes | Yes | Yes | 3rd SHUNT RELEASE/OFLO | [8 empty] | F | 24Vdc | Yes | Yes | Yes |  |  |  | Yes
[15 empty] | COMMAND SHUNT RELEASE [3] | [8 empty] | Character | Description | EGG | EGG, EGR | EGG | EGL | EGT | EGR ME07 S10/20 | EGR ME07 S30/40 | J | 120 Vac/dc | Yes | Yes | Yes |  |  |  | Yes
[15 empty] | 3 | 24 Vdc | Yes | Yes | Yes |  | Yes |  |  |  |  | UL | ANSI | IEC |  |  |  |  | U | 240 Vac/dc | Yes | Yes | Yes |  |  |  | Yes
[15 empty] | 4 | 30 Vdc | Yes | Yes | Yes |  | Yes |  |  | SHUNT RELEASE
[15 empty] | 8 | 48 Vac/dc | Yes | Yes | Yes |  | Yes |  |  | A | 24 Vdc |  |  | Yes
[15 empty] | N | 110-130 Vac/dc | Yes | Yes | Yes |  | Yes |  |  | B | 30 Vdc |  |  | Yes
[15 empty] | W | 220-240 Vac/dc | Yes | Yes | Yes |  | Yes |  |  | C | 48 Vac/dc |  |  | Yes
[15 empty] | Y | 250 Vdc, 250-277 Vac | Yes | Yes | Yes |  | Yes |  |  | D | 60-72 Vdc |  |  | Yes
[18 empty] | OPEN FUSE LOCK OUT (2) | [5 empty] | E | 110-130 Vac/dc |  |  | Yes
[15 empty] | 2 | 240V System Voltage |  | Yes | [5 empty] | F | 208 Vac
[13 empty] | DO NOT INCLUDE |  | 6 | 480V System Voltage |  | Yes | [5 empty] | G | 220-240 Vac/dc |  |  | Yes
[13 empty] | dmh/ABB |  | 9 | 600V System Voltage |  | Yes | [5 empty] | H | 250 Vdc, 250-277 Vac |  |  | Yes
[15 empty] | Notes: | [8 empty] | K | 380-415 Vac |  |  | Yes
[15 empty] | [1] Not available on a switch | [8 empty] | L | 440 Vac |  |  | Yes
[15 empty] | (2) Only for EGR | [8 empty] | M | 24 Vdc | Yes | Yes
[15 empty] | (3) Command Shunt Release Requires GTU Firmware 08.00.30 or newer | [8 empty] | P | 48 Vac/dc | Yes | Yes
[24 empty] | Q | 72 Vdc | Yes | Yes
[24 empty] | R | 120 Vac/dc | Yes | Yes
[24 empty] | S | 208 Vac | Yes | Yes
[24 empty] | T | 240 Vac | Yes | Yes
[24 empty] | V | 250 Vdc | Yes | Yes
[24 empty] | X | None | Yes | Yes | Yes | Yes | Yes
SHUNT RELEASE - NON-CONTINUOUSLY RATED
[24 empty] | F | 24Vdc | Yes | Yes | Yes
[24 empty] | J | 120 Vac/dc | Yes | Yes | Yes
[24 empty] | U | 240 Vac/dc | Yes | Yes | Yes
Project on hold

## DIGITS 12-15 ACC2
EntelliGuard G, L, T, and R Families Breaker/Switch Nomenclature (12-15)
Back
| DIGIT 12 | [23 empty] | DIGIT 13 | [18 empty] | DIGIT 14 | [19 empty] | DIGIT 15 (11) | [11 empty] | Continue for IEC…
| AUX SWITCH AND COIL SIGNALING CONTACTS | [23 empty] | BELL ALARM (BA), READY TO CLOSE CONTACTS (RTC), AND OPERATIONS COUNTER | [18 empty] | KEY LOCKS & PUSHBUTTON PADLOCKS | [19 empty] | MECHANICAL INTERLOCK & Hidden On Button & Neutral CT Adapter
| Character | Aux Switch |  |  |  |  | Coil Signaling Contact (3], [5) | [10 empty] | EGG | EGG EGR | EGG | EGL | EGT | EGR ME07 S10/20 | EGR ME07 S30/40 | Character | Bell Alarm [1] |  |  |  | Counter |  | Ready to Close Contacts [2] | [6 empty] | EGG | EGG, EGR |  | EGL | EGT | Character | Lock Provision Type [2] |  |  |  |  | Mounted Lock Type [1][2] |  |  |  |  | PB Padlocks Installed [3] |  | EGG | EGG, EGR | EGG | EGL | EGT | EGR ME07 S10/20 | EGR ME07 S30/40 | Character | Description | Mech [7] Interlock | Hidden On | Neutral CT Adapter [10] | EGG |  | EGR | EGG, EGR | EGL | EGT | EGR MPACT/ME07
|  | 3NO+3NC (Power Rated) [1] | 4NO+4NC (Power Rated) | 8NO+8NC (Power Rated) [2] | 3NO+3NC (Power Rated)+ 2NO+2NC (Signal Rated) | 4NO+4NC (Power Rated)+ 4NO+4NC (Signal Rated) [2] | None | 1 NO Power Rated thru SD - CC or CCC | 1 NO High Fidelity thru SD - CC or CCC | 1 NO Power Rated on SD - 1st ST | 1 NO High Fidelity thru SD - 1st ST | 1 NO Power Rated on SD - 1st UVR | 1 NO High Fidelity thru SD - 1st UVR | 1 NO Power Rated on SD - 2nd ST or UVR | 1 NO High Fidelity thru SD - 2nd ST or UVR | 1 NO Power Rated on SD - All Devices | 1 NO High Fidelity thru SD - All Devices | [8 empty] | 1 Form C, Power Rated | 1 Form C, Signal Rated | 2 Form C, Power Rated [5] | None | Installed | None | 1NO, Power Rated, Thru SD | 1NO, Signal Rated, Thru SD | 1NO, Signal Rated, Thru TU [4] | 1NC, Power Rated, Thru SD | 1NC, Signal Rated, Thru SD | 1NC, Signal Rated, Thru TU [4] | None | [6 empty] | Profalux | Ronis | Kirk | Castell(4) | None | Profalux | Ronis | Kirk | Castell(4) | None |  |  | UL | ANSI | IEC | [9 empty] | UL | ANSI (11) |  | IEC |  |  |  | Continue for UL/ANSI…
[64 empty] | 1 | Mechanical Interlock - Type A [1] or Type D [4] (B1 or B3) [5] | X |  |  | Yes |  |  | Yes | Yes | Yes
[64 empty] | 2 | Mechanical Interlock - Type B [2] | X |  |  | Yes |  |  | Yes | Yes | Yes
[64 empty] | 3 | Mechanical Interlock - Type C [3] | X |  |  | Yes |  |  | Yes | Yes | Yes
[64 empty] | 4 | Mechanical Interlock - Type D [4] (B2 Only) [5] | X |  |  | Yes |  |  | Yes | Yes | Yes
[18 empty] | UL | ANSI | IEC | [18 empty] | UL | ANSI | IEC | [13 empty] | Yes | No | [7 empty] | 5 | Hidden On Only [8] [9] |  | X |  | Yes |  | Yes
[44 empty] | P | X | [8 empty] | X |  | X | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 6 | Hidden On [9] + Mechanical Interlock - Type A [1] or Type D [4] (B1 or B3) [5] | X | X |  | Yes
[44 empty] | R |  | X | [7 empty] | X |  | X | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 7 | Hidden On [9] + Mechanical Interlock - Type B [2] | X | X |  | Yes
[44 empty] | K |  |  | X | [6 empty] | X |  | X | Yes | Yes | [5 empty] | 8 | Hidden On [9] + Mechanical Interlock - Type C [3] | X | X |  | Yes
[44 empty] | C |  |  |  | X | [5 empty] | X |  | X | Yes | Yes | Yes |  |  |  | Yes | 9 | Hidden On [9] + Mechanical Interlock - Type D [4] (B2 Only) [5] | X | X |  | Yes
[44 empty] | X |  |  |  |  | X |  |  |  |  | X |  | X | Yes | Yes | Yes | Yes | Yes | Yes | Yes | H | Hidden On [9] + GF 4 wire application - Neutral CT adaptor [6] |  | X | X |  |  | Yes
| 2 | X |  |  |  |  | X | [10 empty] | Yes |  |  | Yes | Yes | Yes | Yes | G | X |  |  |  | X |  | X | [6 empty] | Yes |  |  | Yes | Yes | L |  |  |  |  | X |  |  |  |  | X | X |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | N | GF 4 wire application - Neutral CT adaptor [6] |  |  | X |  |  | Yes
| 3 |  | X |  |  |  | X | [13 empty] | Yes | Yes | Yes |  | H | X |  |  |  | X |  |  | X | [5 empty] | Yes |  |  |  | Yes | 4 | X | [8 empty] | X | X |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | X | None |  |  |  | Yes |  | Yes | Yes | Yes | Yes | Yes
| 4 |  |  | X[4] |  |  | X | [10 empty] | Yes | [5 empty] | Yes | J | X |  |  |  | X |  |  |  | X |  |  |  |  | Yes |  |  |  | Yes | 3 |  | X | [7 empty] | X | X |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Notes:
| 6 |  |  |  | X |  | X | [10 empty] | Yes | [5 empty] | Yes | C | X |  |  |  | X | [7 empty] | X | Yes |  |  | Yes | Yes | 2 |  |  | X | [6 empty] | X | X |  | Yes | Yes | [5 empty] | [1] Type A requires 2 cables to be ordered seperately based on relative position of breakers
| 8 |  |  |  |  | X[4] | X | [10 empty] | Yes | [5 empty] | Yes | D | X |  |  |  |  | X | X | [6 empty] | Yes |  |  | Yes | Yes | 1 |  |  |  | X | [5 empty] | X | X |  | Yes | Yes | Yes |  |  |  | Yes | [2] Type B requires 6 cables to be ordered based on relative position of breakers
| A | X | [5 empty] | X | [9 empty] | Yes | [6 empty] | E | X |  |  |  |  | X |  | X | [5 empty] | Yes |  |  |  | Yes | Q | X |  |  |  |  | X | [5 empty] | X | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [3] Type C requires 6 cables to be ordered based on relative position of breakers
| J |  |  |  | X |  |  | X | [9 empty] | Yes | [6 empty] | F | X |  |  |  |  | X |  |  | X |  |  |  |  | Yes |  |  |  | Yes | S |  | X |  |  |  |  | X |  |  |  |  | X | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [4] Type D requires 4 cables to be ordered based on relative position of breakers
| B | X | [6 empty] | X | [8 empty] | Yes | [6 empty] | A | X |  |  |  |  | X | [6 empty] | X | Yes |  |  | Yes | Yes | D |  |  | X |  |  |  |  | X |  |  |  | X | Yes | Yes | [5 empty] | [5] Reference DET-653 Table 4-20 or DEH-41358 Section 3.3
| K |  |  |  | X |  |  |  | X | [8 empty] | Yes | [6 empty] | U |  | X |  |  | X |  | X | [6 empty] | Yes |  |  |  | Yes | F |  |  |  | X |  |  |  |  | X |  |  | X | Yes | Yes | Yes |  |  |  | Yes | [6] This option is for EntelliGuard R (AKD8 & 10) or AKD5 & AKD6 where a MVT Conversion kit was installed
| C | X | [7 empty] | X | [7 empty] | Yes | [6 empty] | V |  | X |  |  | X |  |  | X | [5 empty] | Yes |  |  |  | Yes | 6 | X |  |  |  |  | X |  |  |  |  | X |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [7] Mechanical Interlock not available for Retrofill breaker.
| L |  |  |  | X |  |  |  |  | X | [7 empty] | Yes | [6 empty] | Y |  | X |  |  | X |  |  |  | X |  |  |  |  | Yes |  |  |  | Yes | 7 |  | X |  |  |  |  | X |  |  |  | X |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | [8] Hidden On option is available for Retrofill. Select character 5 or H
| D | X | [8 empty] | X | [6 empty] | Yes | [6 empty] | T |  | X |  |  | X | [7 empty] | X | Yes |  |  |  | Yes | J |  |  | X |  |  |  |  | X |  |  | X |  | Yes | Yes | [5 empty] | [9] Hidden On option is NOT available when PB Padlocks are selected
| M |  |  |  | X | [5 empty] | X | [6 empty] | Yes | [6 empty] | P |  | X |  |  |  | X | X | [6 empty] | Yes |  |  |  | Yes | N |  |  |  | X |  |  |  |  | X |  | X |  | Yes | Yes | Yes |  |  |  | Yes | [10] Neutral CT Adapter requires a trip unit with Ground Fault
| E | X | [9 empty] | X | [5 empty] | Yes | [6 empty] | R |  | X |  |  |  | X |  | X | [5 empty] | Yes |  |  |  | Yes | Notes: | [19 empty] | [11] Mechanical Interlocks and NCT Adapter not available for AKD20 Breakers
| N |  |  |  | X | [6 empty] | X | [5 empty] | Yes | [6 empty] | S |  | X |  |  |  | X |  |  | X |  |  |  |  | Yes |  |  |  | Yes | [1] Lock will have random lock cylinder number. Cannot be coordinated | [19 empty] | Available Cables (reference only)
| F | X | [10 empty] | X |  |  |  |  | Yes | [6 empty] | N |  | X |  |  |  | X | [6 empty] | X | Yes |  |  |  | Yes | [2] For drawout breakers and EGR AKD-5, add as cassette accessory. Not available for drawout breakers. | [19 empty] | GCB1 | Ent.Guard Interlock cable length 1 metre |  |  |  | Not Yet |  |  | Yes
| P |  |  |  | X | [7 empty] | X |  |  |  |  | Yes | [6 empty] | 8 |  |  | X |  | X |  | X | [6 empty] | Yes |  |  |  |  | [3] PB Padlocks are not available when Hidden On option is selected | [19 empty] | GCB2 | Ent.Guard Interlock cable length 1.6 metre |  |  |  | Not Yet |  |  | Yes
| G | X | [11 empty] | X |  |  |  | Yes | [6 empty] | 9 |  |  | X |  | X |  |  | X | [5 empty] | Yes |  |  |  |  | [4] Castell locks for EGG and EGR are FS1 | [19 empty] | GCB3 | Ent.Guard Interlock cable length 2 metre |  |  |  | Not Yet |  |  | Yes
| Q |  |  |  | X | [8 empty] | X |  |  |  | Yes | [6 empty] | Q |  |  | X |  | X |  |  |  | X |  |  |  |  | Yes | [24 empty] | GCB4 | Ent.Guard Interlock cable length 2.5 metre |  |  |  | Not Yet |  |  | Yes
| H | X | [12 empty] | X |  |  | Yes | [6 empty] | 7 |  |  | X |  | X | [7 empty] | X | Yes | [24 empty] | GCB5 | Ent.Guard Interlock cable length 3 metre |  |  |  | Not Yet |  |  | Yes
| R |  |  |  | X | [9 empty] | X |  |  | Yes | [6 empty] | K |  |  |  | X | X |  | X | [6 empty] | Yes |  |  | Yes | Yes | [20 empty] | GCB6 | Ent.Guard Interlock cable length 3.5 metre |  |  |  | Not Yet |  |  | Yes
| S | X | [13 empty] | X |  | Yes | [6 empty] | L |  |  |  | X | X |  |  | X | [5 empty] | Yes |  |  |  | Yes | [20 empty] | GCB7 | Ent.Guard Interlock cable length 4 metre |  |  |  | Not Yet |  |  | Yes
| U |  |  |  | X | [10 empty] | X |  | Yes | [6 empty] | M |  |  |  | X | X |  |  |  | X |  |  |  |  | Yes |  |  |  | Yes
| T | X | [14 empty] | X | Yes | [6 empty] | B |  |  |  | X | X | [7 empty] | X | Yes |  |  | Yes | Yes
| V |  |  |  | X | [11 empty] | X | Yes | [6 empty] | 1 |  |  |  | X |  | X | X | [6 empty] | Yes |  |  | Yes | Yes
| Notes: | [23 empty] | 2 |  |  |  | X |  | X |  | X | [5 empty] | Yes |  |  |  | Yes
| General: This character affects the SD assignment. Refer to 10101883P1 and 11112222P1 | [23 empty] | 3 |  |  |  | X |  | X |  |  | X |  |  |  |  | Yes |  |  |  | Yes
| [1] Standard | [23 empty] | 4 |  |  |  | X |  | X |  |  |  | X |  |  |  | Yes |  |  |  | Yes
| [2] Not available for Side mounted Secondary Disconnects | [23 empty] | 5 |  |  |  | X |  | X |  |  |  |  | X |  |  | Yes |  |  |  | Yes
| [3] Must have Communication on Trip Unit to get Coil Signaling indication via Trip Unit | [23 empty] | 6 |  |  |  | X |  | X | [5 empty] | X |  | Yes |  |  |  | Yes
| [4] Not available when digit 9 = 1 OR Envelope 1 SSD breakers | [23 empty] | X |  |  |  | X |  | X | [6 empty] | X | Yes |  |  | Yes | Yes
| [5] Close Coil Signaling contacts come with 1 switch to feed the TU and 1 to the Secondary Disconnect. Block B is required | [23 empty] | Notes:
| CC - Close Coil | [23 empty] | [1] Bell alarm is not available with Non-Auto CB/Switches
| CCC - Command Close Coil | [23 empty] | [2] Ready to Close via trip unit is not available with Non-Auto CB/Switches
| ST - Shunt Trip | [23 empty] | [3] Not available for external sale. Developed for GE services.
| UVR - Under Voltage Release | [23 empty] | [4] Requires Communications option on Trip Unit
| SD - Secondary Disconnect | [23 empty] | [5] SD required for double bell alarm
| TU - Trip Unit | [23 empty] | SD - Secondary Disconnect
TU - Trip Unit
A
7
N
B
C
T
1
2
3
4
5
6
D
P
K
G
U
E
R
L
H
V
F
S
M
J
Y
X
i
o
q
w
z
8
9
0

## DIGITS 16-19, IEC GTU
EntelliGuard G, L, and T Families Breaker/Switch Nomenclature (IEC 16-19)
Back
IEC Nomenclature Variant
|  | DIGIT 16 |  | DIGITS 17, 18 | [40 empty] | DIGIT 19 |  | Complete Cat #
|  | Character | TRIP UNIT BASIC TYPE | TRIP UNIT FUNCTIONALITY | [40 empty] | MANUAL LANGUAGE OR FIELD INSTALL
| General Note: |  | Description | Character | Delays | [12 empty] | Ground & Earth Fault | [6 empty] | Advanced Features | [11 empty] | Comm. |  |  | Availability |  |  |  |  | Character | Description
| FOR SWITCHES USE "XXX" |  |  |  | L non-switchable | J non-switchable | J switchable | S non-switchable | S Switchable | I switchable | H switchable | G non-switchable | G switchable | C swtichable | D | A switchable | E non-switchable | GF | GFDB | EF | GF+EF | GFA+EFA | STDB.EF(U.K.) | OV on ZSI out | ZSI (ST,GF) | ZSI (ST,GF,I) | ZSI (ST,GFA,I) | ZSI(ST,EFA,I) | ZSI (ST,GF,HI) | ZSI(ST,GFA,HI) | ZSI(ST,EF,HI) | ZSI(ST,EF,HI) | Monitoring | RELT | Data Acquisition | Relaying Package | Modbus | Profibus | Auto/Manual Lockout | EGG | EGL1 | EGLR | EGT | EGR | A | English, German, Italian
[45 empty] | B | English, Dutch, French
[45 empty] | E | English, Spanish, Portuguese
[45 empty] | C | English, Polish, Russian
[45 empty] | Z | Field Install
|  | L | GT-L with Ammeter
|  |  |  | 1 | Yes |  |  | Yes | [30 empty] | Yes |  | Yes
|  |  |  | 2 | Yes |  |  | Yes |  |  |  | Yes | Yes |  |  |  |  | Yes | Yes | [19 empty] | Yes |  | Yes
|  |  |  | 6 | Yes |  |  | Yes |  | Yes | [28 empty] | Yes |  | Yes
|  |  |  | 7 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [19 empty] | Yes |  | Yes
|  | E | GT-E with Ammeter | 0 |  |  |  | Yes | [30 empty] | Yes | Yes |  |  | Yes | Yes
|  |  |  | 1 | Yes |  |  | Yes | [30 empty] | Yes | Yes |  |  | Yes | Yes
|  |  |  | 2 | Yes |  |  | Yes |  |  |  | Yes | Yes |  |  |  |  | Yes | Yes | [19 empty] | Yes | Yes |  |  | Yes | Yes
|  | S | GT-S with Ammeter + Optional Communications | 3 | Yes |  |  | Yes |  |  | Yes | Yes | Yes |  |  |  |  | Yes | Yes | [19 empty] | Yes | Yes |  |  | Yes | Yes
|  |  |  | 5 | Yes |  |  | Yes |  |  | Yes | Yes | Yes |  |  |  |  | Yes | Yes | [17 empty] | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 6 | Yes |  |  | Yes |  | Yes | [28 empty] | Yes | Yes |  |  | Yes | Yes
|  |  |  | 7 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [19 empty] | Yes | Yes |  |  | Yes | Yes
|  |  |  | 9 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [17 empty] | Yes |  | Yes | Yes |  |  | Yes | Yes
|  | N | GT-N with Ammeter + Optional Communication | 3 | Yes |  |  | Yes |  | Yes | [23 empty] | Yes |  |  | Yes |  | Yes |  | Yes
|  |  |  | 4 | Yes |  |  | Yes |  |  | Yes | Yes | Yes |  |  |  |  | Yes | Yes | [13 empty] | Yes | Yes |  |  |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 5 | Yes |  |  | Yes |  | Yes | [22 empty] | Yes | Yes |  |  |  |  | Yes |  | Yes
|  |  |  | 6 | Yes |  |  | Yes |  | Yes | [22 empty] | Yes | Yes |  | Yes |  |  | Yes |  | Yes
|  |  |  | 7 | Yes |  |  | Yes |  | Yes |  | Yes | Yes | [19 empty] | Yes | Yes |  | Yes |  |  | Yes |  | Yes
|  |  |  | 8 | Yes |  |  | Yes |  | Yes | [22 empty] | Yes | Yes |  |  |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 10 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [13 empty] | Yes | Yes |  |  |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 11 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 12 | Yes |  |  | Yes |  |  | Yes | Yes | Yes |  |  |  |  | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  |  | Yes | Yes
|  | H | GT-H with Measurement + Relaying + Waveform Capture + Optional Communications | 4 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [5 empty] | Yes | [13 empty] | Yes |  | Yes
|  |  |  | 8 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [6 empty] | Yes | [12 empty] | Yes |  | Yes
|  |  |  | 10 | Yes |  |  | Yes |  | Yes | [22 empty] | Yes | Yes | Yes |  | Yes |  | Yes |  | Yes
|  |  |  | 11 | Yes |  |  | Yes |  | Yes | [22 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes |  | Yes
|  |  |  | 12 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [13 empty] | Yes | Yes | Yes |  | Yes |  | Yes |  | Yes
|  |  |  | 13 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 14 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 15 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 16 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes |  |  |  | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 17 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 18 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 19 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 20 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 21 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes |  |  | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 22 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes |  |  | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 23 |  |  | Yes |  | Yes | Yes | [22 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 24 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 25 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 26 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 27 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [6 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 28 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [6 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 29 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [6 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 30 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 31 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 32 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 33 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [5 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 34 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [5 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 35 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [5 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 36 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [16 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 37 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [16 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 38 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes |  |  |  |  | Yes | [11 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 39 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes |  |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 40 |  |  |  |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes |  | Yes | [9 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  | Yes
|  |  |  | 50 |  |  |  |  | Yes | Yes |  |  | Yes | Yes | Yes |  |  |  |  | Yes |  |  | Yes | [9 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes |  |  | Yes
|  |  |  | 51 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes | [9 empty] | Yes |  |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 52 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes |  |  | Yes | [6 empty] | Yes |  |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 53 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes | [9 empty] | Yes |  |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 54 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes | [5 empty] | Yes |  |  |  | Yes |  |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 55 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes | [9 empty] | Yes |  | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 56 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes |  |  | Yes | [6 empty] | Yes |  | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 57 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes | [9 empty] | Yes |  | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 58 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes | [7 empty] | Yes |  | Yes |  | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 59 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes | [9 empty] | Yes |  |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 60 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes |  |  | Yes | [6 empty] | Yes |  |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 61 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes | [9 empty] | Yes |  |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 62 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [6 empty] | Yes | [8 empty] | Yes | Yes |  |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 63 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes |  | Yes | [8 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes
|  | P | Inverter High Frequency Filtering Option | 1 | Yes |  |  | Yes | [30 empty] | Yes
|  |  |  | 2 | Yes |  |  | Yes |  |  |  | Yes | Yes |  |  |  |  | Yes | Yes | [19 empty] | Yes
|  |  |  | 6 | Yes |  |  | Yes |  | Yes | [28 empty] | Yes
|  |  |  | 7 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [19 empty] | Yes
|  |  |  | 3 | Yes |  |  | Yes |  |  | Yes | Yes | Yes |  |  |  |  | Yes | Yes | [19 empty] | Yes | Yes |  |  | Yes | Yes
|  |  |  | 5 | Yes |  |  | Yes |  |  | Yes | Yes | Yes |  |  |  |  | Yes | Yes | [17 empty] | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 9 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [17 empty] | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 4 | Yes |  |  | Yes |  |  | Yes | Yes | Yes |  |  |  |  | Yes | Yes | [13 empty] | Yes | Yes |  |  |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 8 | Yes |  |  | Yes |  | Yes | [22 empty] | Yes | Yes |  |  |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 10 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [13 empty] | Yes | Yes |  |  |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 11 | Yes |  |  | Yes |  | Yes |  | Yes | Yes |  |  |  |  | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 12 | Yes |  |  | Yes |  |  | Yes | Yes | Yes |  |  |  |  | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 13 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 14 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 15 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 16 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes |  |  |  | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 17 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes |  |  |  | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 18 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 19 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 20 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 21 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes |  |  | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 22 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes |  |  | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 23 |  |  | Yes |  | Yes | Yes | [22 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 24 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 25 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 26 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 27 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [6 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 28 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [6 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 29 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [6 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 30 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 31 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 32 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [10 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 33 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [5 empty] | Yes | Yes |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 34 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [5 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 35 |  |  | Yes |  | Yes | Yes |  |  | Yes | Yes | Yes | Yes | [5 empty] | Yes |  |  |  |  | Yes | [5 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 36 |  |  | Yes |  | Yes | Yes | [22 empty] | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 37 |  |  | Yes |  | Yes | Yes | [22 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 38 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | [5 empty] | Yes | [11 empty] | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 39 |  |  | Yes |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes | [5 empty] | Yes | [7 empty] | Yes |  |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 51 |  |  | Yes |  | Yes | Yes |  |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes | [8 empty] | Yes |  |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 52 |  |  | Yes |  | Yes | Yes |  |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes |  | Yes | [6 empty] | Yes |  |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 53 |  |  | Yes |  | Yes |  | Yes |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes | [8 empty] | Yes |  |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 54 |  |  | Yes |  | Yes |  | Yes |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes |  |  |  |  | Yes |  |  |  | Yes |  |  | Yes |  |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 55 |  |  | Yes |  | Yes | Yes |  |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes | [8 empty] | Yes |  | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 56 |  |  | Yes |  | Yes | Yes |  |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes |  | Yes | [6 empty] | Yes |  | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 57 |  |  | Yes |  | Yes |  | Yes |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes | [8 empty] | Yes |  | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 58 |  |  | Yes |  | Yes |  | Yes |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes | [6 empty] | Yes |  | Yes |  | Yes | Yes | Yes |  | Yes | Yes |  |  | Yes | Yes
|  |  |  | 59 |  |  | Yes |  | Yes | Yes |  |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes | [8 empty] | Yes |  |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 60 |  |  | Yes |  | Yes | Yes |  |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes |  | Yes | [6 empty] | Yes |  |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 61 |  |  | Yes |  | Yes |  | Yes |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes | [8 empty] | Yes |  |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  |  |  | 62 |  |  | Yes |  | Yes |  | Yes |  |  |  | Yes |  | Yes | [5 empty] | Yes | Yes | [7 empty] | Yes | Yes |  |  | Yes |  | Yes | Yes | Yes |  |  | Yes | Yes
|  | Notes: | 1. For LI breakers only GT-H/N are available
2. IEC GF protection is always switchable
General: This character affects the SD assignment. Refer to 10101883P1 and 11112222P1

## DIGITS 16-20, UL_ANSI GTU
EntelliGuard G, L, T and R Families Breaker/Switch Nomenclature (UL/ANSI 16-20)
Back
UL/ANSI Nomenclature Variant
|  | DIGIT 16, 17 |  | DIGIT 18 |  | DIGIT 19 |  | DIGIT 20 |  | Complete Cat #
|  | GLOBAL TRIP UNIT OVERCURRENT PROTECTION TYPE |  | ZSI OPTION |  | ADVANCED FUNCTIONS |  | RATING PLUG
|  | Character | Description | Character | Description | Character | Description | Character | Description
|  | XX | None [1] | Z | ZSI, Short time and GF; user selectable | 1 | Reduced Energy Let-Through (RELT) | X | None [1] | Continue to 18 Digit Proposal for UL/ANSI…
|  | L1 | RESERVED | T | Z + IOC or HIOC ZSI; user selectable | 2 | Modbus Protocol + RELT | A | RESERVED
|  | L2 | RESERVED | V | RESERVED | 3 | Profibus Protocol + RELT | B | 150
|  | L3 | LSI (S, switchable) (I, switchable ANSI only) | W | RESERVED | 4 | Monitoring + RELT, NO Communication | C | 200
|  | L4 | LSIG (S, switchable) (I, switchable ANSI only) | X | None [1] | 5 | Monitoring + Relay Package + RELT | D | 225
|  | L5 | LSIGA (S, switchable) (I, switchable ANSI only) | Notes: |  | 6 | Monitoring + Data Acquisition, Modbus Protocol + RELT | E | 250
|  | L6 | LSIC (S, switchable) (I, switchable ANSI only) |  | General: This character affects the SD assignment. Refer to 10101883P1 and 11112222P1 | 7 | Monitoring + Data Acquisition, Profibus Protocol + RELT | F | 300
|  | L7 | LSICA (S, switchable) (I, switchable ANSI only) |  | [1] Only available option for switches | 8 | Monitoring + Data Acquisition + Relay Package, Modbus + RELT | G | 350
|  | L8 | LSIGDA [2] (S, G, A all switchable) (I, switchable ANSI only) |  |  | 9 | Monitoring + Data Acquisition + Relay Package, Profibus + RELT | H | 400
|  | L9 | LSIGCDA [2] (S, G, C, A all switchable) (I, switchable ANSI only) |  |  | X | None [1], [2] | I | 450
|  | LA | RESERVED |  |  | Notes: |  | J | 500
|  | LB | RESERVED |  |  |  | General: This character affects the SD assignment. Refer to 10101883P1 and 11112222P1 | K | 600
|  | LC | LSH (S, switchable) (H, switchable ANSI only) |  |  |  | [1] Only available option for switches | M | 700
|  | LD | LSHG (S, switchable) (H, switchable ANSI only) |  |  |  | [2] X is not an option for GE internal 5000A and 6000A ANSI Breakers and Switches | N | 750
|  | LE | LSHGA (S, switchable) (H, switchable ANSI only) |  |  |  |  | O | 800
|  | LF | LSHC (S, switchable) (H, switchable ANSI only) |  |  |  |  | P | 900
|  | LG | LSHCA (S, switchable) (H, switchable ANSI only) |  |  |  |  | Q | 1000
|  | LH | LSHGDA [2] (S, G, A all switchable) (H, switchable ANSI only) |  |  |  |  | R | 1100
|  | LK | LSHGCDA [2] (S, G, C, A all switchable) (H, switchable ANSI only) |  |  |  |  | S | 1200
|  | LM | Inverter Filtering - LSI (S, switchable) (I, switchable ANSI only) |  |  |  |  | U | 1500
|  | LN | Inverter Filtering - LSIG (S, switchable) (I, switchable ANSI only) |  |  |  |  | V | 1600
|  | LP | Inverter Filtering - LSHGCDA [2] (S, G, C, A all switchable) (H, switchable ANSI only) |  |  |  |  | W | 1900
|  | LQ | RESERVED |  |  |  |  | Y | 2000
|  | LR | RESERVED |  |  |  |  | Z | 2200
|  | LS | RESERVED |  |  |  |  | 1 | 2400
|  | LT | RESERVED |  |  |  |  | 2 | 2500
|  | LU | RESERVED |  |  |  |  | 3 | 3000
|  | LV | RESERVED |  |  |  |  | 4 | 3200
|  | LW | G (PB II Switch and EntelliGuard Switch GF Relay only, FUTURE) |  |  |  |  | 5 | 3600
|  | LY | GA (PB II Switch and EntelliGuard Switch GF Relay only, FUTURE) |  |  |  |  | 6 | 4000
|  | With Fuse Settings | [5 empty] | 7 | 5000
|  | J1 | RESERVED |  |  |  |  | 8 | 6000
|  | J2 | RESERVED |  |  |  |  | 9 | UNIV
|  | J3 | JSI (S, switchable) (I, switchable ANSI only) |  |  |  |  | 0 | No Rating Plug (Mpact only) **
|  | J4 | JSIG (S, switchable) (I, switchable ANSI only) |  |  |  |  | Notes:
|  | J5 | JSIGA (S, switchable) (I, switchable ANSI only) | [5 empty] | [1] Only available option for switches. Not available for breakers
|  | J6 | JSIC (S, switchable) (I, switchable ANSI only)
|  | J7 | JSICA (S, switchable) (I, switchable ANSI only)
|  | J8 | JSIGDA* (S, G, A all switchable) (I, switchable ANSI only)
|  | J9 | JSIGCDA* (S, G, C, A all switchable) (I, switchable ANSI only)
|  | JA | RESERVED
|  | JB | RESERVED
|  | JC | JSH (S, switchable) (H, switchable ANSI only)
|  | JD | JSHG (S, switchable) (H, switchable ANSI only)
|  | JE | JSHGA (S, switchable) (H, switchable ANSI only)
|  | JF | JSHC (S, switchable) (H, switchable ANSI only)
|  | JG | JSHCA (S, switchable) (H, switchable ANSI only)
|  | JH | JSHGDA* (S, G, A all switchable) (H, switchable ANSI only)
|  | JK | JSHGCDA* (S, G, C, A all switchable) (H, switchable ANSI only)
|  | JM | RESERVED
|  | JN | RESERVED
|  | JP | RESERVED
|  | JQ | RESERVED
|  | JR | RESERVED
|  | JS | RESERVED
|  | JT | RESERVED
|  | JU | RESERVED
|  | JV | RESERVED
|  | JW | RESERVED
|  | JY | RESERVED
Notes:
[1] Only available option for switches
[2] Not UL approved

## 20 to 18, UL_ANSI CONVERSION
EntelliGuard G, L, T, and R Families Breaker/Switch Nomenclature (UL/ANSI 16-18)
Back
UL/ANSI Nomenclature Variant
|  |  |  | DIGIT 16 |  | DIGIT 17 | [10 empty] | DIGIT 18 |  | Complete Cat #
|  |  |  | GLOBAL TRIP UNIT OVERCURRENT PROTECTION TYPE |  | ZSI + ADVANCED FUNCTIONS | [10 empty] | RATING PLUG
|  |  |  | Character | Description | Character | ZSI |  |  | Advanced Functions | [6 empty] | Character | Description
|  |  |  | X | NONE - (For Switch Only) |  | ZSI (ST, GF) | ZSI+IOC/HIOC | None | RELT | Modbus | Profibus | Monitoring | Relaying | DAQ | None | X | Rating Plug Not Required/Non Auto. Switch
| This is created by the following: |  |  | 3 | LSI (S, switchable) (I, switchable ANSI only) | [11 empty] | A | RESERVED
| 1. Drop Old digit 16 |  |  | 4 | LSIG (S, switchable) (I, switchable ANSI only) | [11 empty] | B | 150
| 2. Convert Old Dig 18&19 as follows |  |  | 5 | LSIGA (S, switchable) (I, switchable ANSI only) | [11 empty] | C | 200
| Old 18,19 | New 17 |  | 6 | LSIC (S, switchable) (I, switchable ANSI only) | A | Yes |  |  | Yes | [6 empty] | D | 225
|  | Z1 | A | 7 | LSICA (S, switchable) (I, switchable ANSI only) | B |  | Yes |  | Yes | [6 empty] | E | 250
|  | T1 | B | 8 | LSIGDA* (S, G, A all switchable) (I, switchable ANSI only) | C |  |  | Yes | Yes | [6 empty] | F | 300
|  | X1 | C | 9 | LSIGCDA* (S, G, C, A all switchable) (I, switchable ANSI only) | D | Yes |  |  | Yes | Yes | [5 empty] | G | 350
|  | Z2 | D | C | LSH (S, switchable) (H, switchable ANSI only) | E |  | Yes |  | Yes | Yes | [5 empty] | H | 400
|  | T2 | E | D | LSHG (S, switchable) (H, switchable ANSI only) | F |  |  | Yes | Yes | Yes | [5 empty] | I | 450
|  | X2 | F | E | LSHGA (S, switchable) (H, switchable ANSI only) | G | Yes |  |  | Yes |  | Yes |  |  |  |  | J | 500
|  | Z3 | G | F | LSHC (S, switchable) (H, switchable ANSI only) | H |  | Yes |  | Yes |  | Yes |  |  |  |  | K | 600
|  | T3 | H | G | LSHCA (S, switchable) (H, switchable ANSI only) | J |  |  | Yes | Yes |  | Yes |  |  |  |  | M | 700
|  | X3 | J | H | LSHGDA* (S, G, A all switchable) (H, switchable ANSI only) | K | Yes |  |  | Yes |  |  | Yes |  |  |  | N | 750
|  | Z4 | K | K | LSHGCDA* (S, G, C, A all switchable) (H, switchable ANSI only) | L |  | Yes |  | Yes |  |  | Yes |  |  |  | O | 800
|  | T4 | L | M | Inverter Filtering - LSI (S, switchable) (I, switchable ANSI only) | M |  |  | Yes | Yes |  |  | Yes |  |  |  | P | 900
|  | X4 | M | N | Inverter Filtering - LSIG (S, switchable) (I, switchable ANSI only) | N | Yes |  |  | Yes |  |  | Yes | Yes |  |  | Q | 1000
|  | Z5 | N | P | Inverter Filtering - LSHGCDA (S, G, C, A all switchable) (H, switchable ANSI only) | P |  | Yes |  | Yes |  |  | Yes | Yes |  |  | R | 1100
|  | T5 | P |  |  | Q |  |  | Yes | Yes |  |  | Yes | Yes |  |  | S | 1200
|  | X5 | Q |  |  | R | Yes |  |  | Yes | Yes |  | Yes |  | Yes |  | U | 1500
|  | Z6 | R |  |  | S |  | Yes |  | Yes | Yes |  | Yes |  | Yes |  | V | 1600
|  | T6 | S |  |  | T |  |  | Yes | Yes | Yes |  | Yes |  | Yes |  | W | 1900
|  | X6 | T |  |  | U | Yes |  |  | Yes |  | Yes | Yes |  | Yes |  | Y | 2000
|  | Z7 | U |  |  | V |  | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Z | 2200
|  | T7 | V |  |  | W |  |  | Yes | Yes |  | Yes | Yes |  | Yes |  | 1 | 2400
|  | X7 | W |  |  | Y | Yes |  |  | Yes | Yes |  | Yes | Yes | Yes |  | 2 | 2500
|  | Z8 | Y |  |  | Z |  | Yes |  | Yes | Yes |  | Yes | Yes | Yes |  | 3 | 3000
|  | T8 | Z |  |  | 2 |  |  | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 4 | 3200
|  | X8 | 2 |  |  | 3 | Yes |  |  | Yes |  | Yes | Yes | Yes | Yes |  | 5 | 3600
|  | Z9 | 3 |  |  | 4 |  | Yes |  | Yes |  | Yes | Yes | Yes | Yes |  | 6 | 4000
|  | T9 | 4 |  |  | 5 |  |  | Yes | Yes |  | Yes | Yes | Yes | Yes |  | 7 | 5000
|  | X9 | 5 |  |  | 6 | Yes | [8 empty] | Yes | 8 | 6000
|  | ZX | 6 |  |  | 7 |  | Yes | [7 empty] | Yes
|  | TX | 7 |  |  | X |  |  | Yes | [6 empty] | Yes
|  | XX | X

## Rating Plug Matrix
Breaker Sensor (A) --> | EntelliGuard G Air Circuit Breaker Rating Plug Logic Matrix (UL489, UL1066, IEC)
| All | UL/ANSI | IEC | All | All | UL/ANSI | IEC | All | All | All | UL | IEC/ANSI | All | All | UL/IEC | IEC |  |  | Entelliguard TU Rating Plugs
| 400 | 600 | 630 | 800 | 1000 | 1200 | 1250 | 1600 | 2000 | 2500 | 3000 | 3200 | 4000 | 5000 | 6000 | 6400
Rating Plugs (Amps) | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 150 | 150 | B | GTP | 0150 | U | 01 | 04
| 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 200 | 200 | C | GTP | 0200 | U | 02 | 04
| 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 225 | 225 | D | GTP | 0225 | U | 03 | 06
| 250 | 250 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 250 | 250 | E | GTP | 0250 | U | 04 | 07
| 300 | 300 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 300 | 300 | F | GTP | 0300 | U | 04 | 08
| 350 | 350 | 350 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 350 | 350 | G | GTP | 0350 | U | 04 | 08
| 400 | 400 | 400 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 400 | 400 | H | GTP | 0400 | U | 04 | 10
| 0 | 450 | 450 | 450 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 450 | 450 | I | GTP | 0450 | U | 06 | 12
| 0 | 500 | 500 | 500 | 500 | 500 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 500 | 500 | J | GTP | 0500 | U | 06 | 13
| 0 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 600 | 600 | K | GTP | 0600 | U | 06 | 16
| 0 | 0 | 630 | 630 | 630 | 630 | 630 | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 630 | 630 *1 | L | GTP | 0630 | U | 07 | 16
| 0 | 0 | 0 | 700 | 700 | 700 | 700 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 700 | 700 | M | GTP | 0700 | U | 08 | 16
| 0 | 0 | 0 | 750 | 750 | 750 | 750 | 750 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 750 | 750 | N | GTP | 0750 | U | 08 | 20
| 0 | 0 | 0 | 800 | 800 | 800 | 800 | 800 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 800 | 800 | O | GTP | 0800 | U | 08 | 20
| 0 | 0 | 0 | 0 | 900 | 900 | 900 | 900 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 900 | 900 | P | GTP | 0900 | U | 10 | 20
| 0 | 0 | 0 | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 1000 | 1000 | Q | GTP | 1000 | U | 10 | 25
| 0 | 0 | 0 | 0 | 0 | 1100 | 1100 | 1100 | 1100 | 1100 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1100 | 1100 | R | GTP | 1100 | U | 12 | 25
| 0 | 0 | 0 | 0 | 0 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 0 | 0 | 0 | 0 | 18 | 1200 | 1200 | S | GTP | 1200 | U | 12 | 32
| 0 | 0 | 0 | 0 | 0 | 0 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 0 | 0 | 0 | 0 | 19 | 1250 | 1250 *1 | T | GTP | 1250 | U | 13 | 32
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 0 | 0 | 0 | 20 | 1500 | 1500 | U | GTP | 1500 | U | 16 | 40
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 0 | 0 | 0 | 21 | 1600 | 1600 | V | GTP | 1600 | U | 16 | 40
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900 | 1900 | 1900 | 1900 | 1900 | 1900 | 0 | 0 | 22 | 1900 | 1900 | W | GTP | 1900 | U | 20 | 50
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 0 | 0 | 23 | 2000 | 2000 | Y | GTP | 2000 | U | 20 | 50
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2200 | 2200 | 2200 | 2200 | 2200 | 0 | 0 | 24 | 2200 | 2200 | Z | GTP | 2200 | U | 25 | 50
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 25 | 2400 | 2400 | 1 | GTP | 2400 | U | 25 | 64
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 26 | 2500 | 2500 | 2 | GTP | 2500 | U | 25 | 64
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 27 | 3000 | 3000 | 3 | GTP | 3000 | U | 30 | 64
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3200 | 3200 | 3200 | 3200 | 3200 | 28 | 3200 | 3200 | 4 | GTP | 3200 | U | 32 | 64
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3600 | 3600 | 3600 | 3600 | 29 | 3600 | 3600 | 5 | GTP | 3600 | U | 40 | 64
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 4000 | 4000 | 4000 | 30 | 4000 | 4000 | 6 | GTP | 4000 | U | 40 | 64
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5000 | 5000 | 5000 | 31 | 5000 | 5000 | 7 | GTP | 5000 | U | 50 | 64
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 6000 | 32 | 6000 | 6000 | 8 | GTP | 6000 | U | 60 | 64
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6400 | 33 | 6400 | 6400 *1 | 9 | GTP | 6400 | U | 64 | 64
*1 IEC Only (IEC uses Universal Rating Plug not these)

## Entellysis Variant
Home
Entellisys Nomenclature Variant
| DIGIT 1 |  | DIGIT 2 |  | DIGITS 3, 4 |  | DIGIT 5 | [7 empty] | DIGIT 6 |  | DIGIT 7 |  | DIGIT 8 |  | DIGITS 9,10 |  | Complete Cat #!
| PRODUCT LINE DEFINITION |  | PRODUCT TYPE |  | CURRENT RATING |  | INTERRUPTION TIER (kA) and Frame Size | [7 empty] | CONSTRUCTION |  | MOTOR OPERATOR |  | ACCESSORY |  | FUTURE
| Character | Description | Character | Description | Character | Description | Description | [7 empty] | Character | Description | Character | Description | Character | Description | Character | Description
[7 empty] | Character | 254V | 508V | 635V | 1/2s W/S | Frame Availability
| E | Entellisys Breaker | E | Entellysis CB | 8 | 800A | [5 empty] | F1 | F2 | F3 | 1 | Envelope 1 | M | Manual | X | None | XX | -
| Notes: |  |  |  | 16 | 1600A | S | 65 | 65 | 50 | 50 | 400-1200 |  |  | 2 | Envelope 2 | E | Electric | B | Bell Alarm
|  | Entellisys is an ANSI/UL1066 product |  |  | 20 | 2000A | N | 65 | 65 | 65 | 65 | 400-2000 | 3200 |  | 3 | Envelope 3 |  |  | N[1][2] | Network Interlock
[5 empty] | 32 | 3200A | H | 85 | 85 | 65 | 65 | 400-2000 | [6 empty] | Notes:
[5 empty] | 40 | 4000A | P | 100 | 100 | 65 | 65 | 400-2000 | [6 empty] | [1] Electric Breakers only (2) NI option includes the Hidden-On Button
[5 empty] | 50 | 5000A | E | 85 | 85 | 85 | 85 |  | 400-3200 | [5 empty] | (2) NI option includes the Hidden-On Button
[7 empty] | M | 100 | 100 | 100 | 85 |  | 400-3200 | 4000-5000
[7 empty] | B | 100 | 100 | 100 | 100 |  |  | 3200-5000
[7 empty] | L | 150 | 150 | 100 | 100 |  |  | 3200-5000
[7 empty] | W | 200 | 200 | 100 | 100 |  |  | 3200-5000

## UL489B Variant
Home
EntelliGuard G UL489B (UL DC Switch & Cassette) Nomenclature Variant
| DIGIT 1 |  | DIGIT 2 |  | DIGITS 3, 4 |  | DIGIT 5 | [9 empty] | DIGIT 6 |  |  | Continue for Breaker Cat #…
| PRODUCT LINE DEFINITION |  | PRODUCT TYPE |  | CURRENT RATING |  | INTERRUPTION TIER (kA) and Frame Size | [9 empty] | CONSTRUCTION
| Character | Description | Character | Description | Character | Description | Character | 240V | 480V | 600V | 600Vdc | 1000Vdc | Frame Availability |  |  |  | Character | Description
[13 empty] | F1 | F2 | F3
| G | EntelliGuard G Breaker & Switch | L | UL489B DC Non-Auto CB | 8 | 800A | M |  |  |  | 125 | 125 |  | 800-3000 |  |  | 1 | OEM Drawout - 3 Pole*
| Notes: |  |  |  | 16 | 1600A | [10 empty] | 2 | OEM Drawout - 4 Pole*
|  | EntelliGuard GL Series is a UL489B product |  |  | 20 | 2000A | [10 empty] | X | OEM Stationary - 3 Pole, No Rear Terminations
[5 empty] | 30 | 3000A | [10 empty] | Y | OEM Stationary - 4 Pole, No Rear Terminations
Notes:
* Not available for cassette
Cassette Variant
[17 empty] | DIGIT 6 |  | DIGIT 7 |  | Complete UL489B Cassette Cat #
[17 empty] | SHUTTERS |  | SHUTTERS
[17 empty] | Character | Description | Character | Description
[17 empty] | X | 3 Pole - No Terminations (order Seperately) | S | Shutter Insalled
[17 empty] | Y | 4 Pole - No Terminations (order Seperately) | X | None

## AK_AKR_WP Retrofill Variant
Home
EntelliGuard R (Retrofill) Nomenclature Variant
| DIGIT 1 |  | DIGIT 2 |  |  | DIGITS 3, 4 [1] | [5 empty] | DIGIT 5 | [87 empty] | DIGIT 6 | [8 empty] | Continue…
| PRODUCT LINE DEFINITION |  | PRODUCT TYPE |  | Electrical Standards | CURRENT RATING | [5 empty] | CONSTRUCTION | [87 empty] | PRIMARY/SECONDARY DISCONNECT CONSTRUCTION |  | Gear Type
| Character | Description | Character | Description |  | Character | Description | Applicability by Product Type (Dig. 2) |  |  |  | Digit 2 = 0 (AKD) | [11 empty] | Digit 2 = 1, 4 (AKD 5 and AKD6 AK25, AK50) | [12 empty] | Digit 2 = 2,5 (AKD 6) | [12 empty] | Digit 2 = 3,6 (AKD 8) | [12 empty] | Digit 2 = 7,8 (AKD 10) | [12 empty] | Digit 2 = 9 (AKD 10 Entellisys) | [9 empty] | Digit 2 = R (ME07) | [13 empty] | Character | Description | AKD | AKD-5 | AKD-6 LF (3) | AKD-6 SF(4) | AKD-8 | AKD-10/ Entellisys | ME07 | ...to 19 digit IEC or 20 digit ANSI
[8 empty] | 0 | 1-8 | 9 | R | Character[4] | Frame Size | GE AKD | AIC w/Inst. (kA) |  |  | AIC w/o Inst. (kA) |  |  | Icw w/ Inst. | Breaker Ratings | Switch Rating | Character[4] | Frame Size | EGG Frame Size | GE/OEM AKD5 and AKD6 AK25,AK50 | AIC w/Inst. (kA) |  |  | AIC w/o Inst. (kA) |  |  | Icw w/ Inst. | Breaker Ratings | Switch Rating | Character[4] | Frame Size | EGG Frame Size | GE/OEM AKD6 | AIC w/Inst. (kA) |  |  | AIC w/o Inst. (kA) |  |  | Icw w/ Inst. | Breaker Ratings | Switch Rating | Character[4] | Frame Size | EGG Frame Size | GE/OEM AKD8 | AIC w/Inst. (kA) |  |  | AIC w/o Inst. (kA) |  |  | Icw w/ Inst. | Breaker Ratings | Switch Rating | Character[4] | Frame Size | EGG Frame Size | GE/OEM AKD10 | AIC w/Inst. (kA) |  |  | AIC w/o Inst. (kA) |  |  | Icw (kA) w/ Inst. | Breaker Ratings | Switch Rating | Character[4] | Frame Size | GE AKD10 Entellisys | AIC w/Inst. (kA) |  |  | AIC w/o Inst. (kA) |  |  | Icw (kA) w/ Inst. | Character | Breaker Ratings | Switch Ratings | ME07/MET07 |  |  | Icu (kA) |  |  |  | Icm (kA) |  |  | Icw (kA)
| R | EntelliGuard R Breaker & Switch [1] | 1 | GE AKD5, GE AKD6 (AK25 and AK50 Only) | ANSI | XX | No Sensor (Switch) |  | Yes |  | Yes |  |  | Breaker Type | 254V | 508V | 635V | 254V | 508V | 635V | [6 empty] | Breaker Type | 254V | 508V | 635V | 254V | 508V | 635V | [6 empty] | Breaker Type | 254V | 508V | 635V | 254V | 508V | 635V | [6 empty] | Breaker Type | 254V | 508V | 635V | 254V | 508V | 635V | [6 empty] | Breaker Type | 254V | 508V | 635V | 254V | 508V | 635V | [5 empty] | Breaker Type | 254V | 508V | 635V | 254V | 508V | 635V |  |  |  |  | Breaker Type | ME Frame | EGG Frame | 415V | 440V | 500V | 690V | 415V | 500V | 690V | @ 0.3s | X | EntelliGuard 78 PT Drawout Secondary Disc (For AKD6, AK25/50 Only) | Yes | Yes | Yes | Yes
| Notes: |  | 2 | GE AKD6 | ANSI | 01 | 150A (Future) |  |  |  |  | A | 225A | AK-1-15 | ? | ? | ? | 15 | 15 | 15 | 15 | 400 | 225 | A | 225A |  | AK-1A-15 | [9 empty] | A | 225A | [11 empty] | A | 225A | [11 empty] | A | 225A | [11 empty] | A | 225A | [8 empty] | A | 400, 630, 800, 1000, 1250 | 630, 800, 1000, 1250 | N | 10 | 0.5 | 30 |  |  |  | 63 |  |  | 30 | 1 | No Sec Disc Bullet or Harnesses (AKR Breakers Only) |  |  |  | Yes | Yes
|  | [1] Drawout Construction only | 3 | GE AKD8 Vertical Lower Stud [1] | ANSI | 02 | 200A |  |  |  |  | B[1] | 225A | AK-15 | ? | ? | ? | 15 | 15 | 15 | 15 | 400 | 225 | B | 225A | [11 empty] | B | 225A | [11 empty] | B | 225A | [11 empty] | B | 225A | [11 empty] | B | 225A | [8 empty] | B | 400, 630, 800, 1000, 1250 | 630, 800, 1000, 1250 | S1 | 10 | 0.5 | 50 |  | 50 | 42 | 105 | 105 | 88.2 | 50 | 2 | A,B,C Bullet Disc Installed (AKR Breakers Only) |  |  |  | Yes | Yes
|  |  | 4 | OEM, AKD5 and AKD6 AK25, AK50 | ANSI | 03 | 225A | Yes |  |  |  | C | 600A | AK-25 | 42 | 42 | 42 | 22 | 22 | 22 | 22 | 400, 600 | 600 | C | 600A | [11 empty] | C | 600A | [11 empty] | C | 600A | [11 empty] | C | 600A | [11 empty] | C | 600A | [8 empty] | C | 400, 630, 800, 1000, 1250 | 630, 800, 1000, 1250 | H | 10 | 0.5 | 65 | 65 | 50 | 42 | 105 | 105 | 88.2 | 50 | 3 | A,B,C Disc & 12 Pin Harness wired (AKR Breakers Only) |  |  |  |  | Yes
|  |  | 5 | OEM, AKD6 | ANSI | 04 | 400A |  | Yes |  | Yes | D | 600A | [10 empty] | D | 600A | 1 | AK-25 | 42 | 42 | 42 | 22 | 22 | 22 | 22 | 400, 600 | 600 | D | 600A | [11 empty] | D | 600A | [11 empty] | D | 600A | [11 empty] | D | 600A | [8 empty] | D | 1600 | 1600 | N | 20 | 0.5 | 35 |  |  |  | 73.5 |  |  | 35 | 4 | A,B,C Disc & 19 Pin Harness wired (AKR Breakers Only) |  |  |  | Yes | Yes
|  |  | 6 | OEM AKD8 Horizontal Lower Stud [1] | ANSI | 06 | 600A |  | Yes |  |  | E | 600A | [10 empty] | E[1],[3] | 600A | 1 | AKU-25 | 100 | 100 | 100 | - | - | - | n/a | 400, 600 | - | E | 600A | [11 empty] | E | 600A | [11 empty] | E | 600A | [11 empty] | E | 600A | [8 empty] | E | 1600 | 1600 | S1 | 20 | 0.5 | 55 |  | 50 | 42 | 105 | 105 | 88.2 | 50 | 5[5] | A,B,C Disc & Legacy 24 Pin Harness wired (AKR Breakers Only) |  |  |  |  | Yes
|  |  | 7 | GE AKD10 | ANSI | 7 | 630A |  |  |  | Yes | F | 600A | AKU-25 | 100 | 100 | 100 | - | - | - | n/a | 400, 600 | - | F | 600A | [11 empty] | F | 600A | [11 empty] | F | 600A | [11 empty] | F | 600A | [11 empty] | F | 600A | [8 empty] | F | 1600 | 1600 | H | 20 | 0.5 | 65 | 65 | 50 | 42 | 105 | 105 | 88.2 | 50 | 6 | 36 Point Secondary Disconnects | [5 empty] | Yes[1]
|  |  | 8 | GE OEM, AKD10 | ANSI | 08 | 800A |  | Yes | Yes | Yes | G | 800A | [10 empty] | G | 800A | [11 empty] | G | 800A | 1 | AKR30, AKR30H | 50 | 42 | 42 | 42 | 42 | 42 | 42 | 400, 600, 800 | 800 | G | 800A | 1 | AKR30, AKR30H | 50 | 42 | 42 | 42 | 42 | 42 | 42 | 400, 600, 800 | 800 | G | 800A | 1 | WavePro WPS-08 | 42 | 30 | 30 | 30 | 30 | 30 | 42 | 400, 800 | 800 | G | 800A | EGS-08 | 42 | 30 | 30 | 30 | 30 | 30 | 30 | G | 2000, 2500 | 2500 | N | 30 | 1 | 40 |  |  |  | 84 |  |  | 40 | 7 | 72 Point Secondary Disconnects | [5 empty] | Yes[1]
|  |  | 9 | GE, AKD10 Entellisys | ANSI | 10 | 1000A |  | Yes |  | Yes | H | 800A | [10 empty] | H | 800A | [11 empty] | H | 800A | 1 | AKRU-30 | 100 | 100 | 100 | - | - | - | n/a | 400, 800 | - | H | 800A | 1 | AKRU-30 | 100 | 100 | 100 | - | - | - | n/a | 800 | - | H | 800A | 1 | WavePro WPH-08 | 50 | 42 | 42 | 42 | 42 | 42 | 42 | 400, 800 | 800 | H | 800A | EGH-08 | 50 | 42 | 42 | 42 | 42 | 42 | 42 | H | 2000, 2500 | 2500 | S1 | 30 | 1 | 65 |  | 65 | 65 | 143 | 143 | 105 | 65 | D | 3 Pole, Drawout | [6 empty] | Yes
|  |  | 0 | GE AKD | ANSI, Not Listed | 12 | 1200A |  | Yes |  |  | I | 800A | [10 empty] | I | 800A | [11 empty] | I | 800A | [11 empty] | I | 800A | 1 | AKR30L | 65 | 65 | 50 | 65 | 65 | 50 | 65 | 400, 600, 800 | 800 | I | 800A | 1 | WavePro WPX-08 | 65 | 65 | 50 | 65 | 65 | 50 | 50 | 400, 800 | 800 | I | 800A | EGX-08 | 65 | 65 | 50 | 65 | 65 | 50 | 65/50[7] | I | 2000, 2500 | 2500 | H | 30 | 1 | 85 | 85 | 65 | 65 | 143 | 143 | 105 | 65 | L | 4 Pole, Left Neutral, Drawout | [6 empty] | Yes[2]
|  |  | A | Federal Pacific (FUTURE) |  | 13 | 1250A |  |  |  | Yes | J | 800A | [10 empty] | J | 800A | [11 empty] | J | 800A | [11 empty] | J | 800A | 1 | AKR30S | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 400, 600, 800 | 800 | J | 800A | [11 empty] | J | 800A | [8 empty] | J | 3200 | 3200 | N | 40 | 2 | 40 |  |  |  | 84 |  |  | 40 | R | 4 Pole, Right Neutral, Drawout | [6 empty] | Yes[2]
|  |  | B | Federal Pacific (FUTURE) |  | 16 | 1600A |  | Yes | Yes | Yes | K | 800A | [10 empty] | K | 800A | [11 empty] | K | 800A | [11 empty] | K[2] | 800A | 1 | AKRU-30S | 100 | 100 | 100 | - | - | - | n/a | 400, 800 | - | K | 800A | 1 | WavePro WPF-08 | 100 | 100 | 100 | - | - | - | n/a | 400, 800 | - | K | 800A | EGF-08 | 100 | 100 | 100 | - | - | - | n/a | K | 3200 | 3200 | S1 | 40 | 2 | 70 |  | 70 | 70 | 154 | 154 | 154 | 70 | Notes:
|  |  | C | Federal Pacific (FUTURE) |  | 20 | 2000A |  | Yes | Yes | Yes | L | 800A | [10 empty] | L | 800A | [11 empty] | L | 800A | [11 empty] | L | 800A | [11 empty] | L | 800A | [11 empty] | L | 800A | [8 empty] | L | 3200 | 3200 | H | 40 | 2 | 100 | 100 | 90 | 80 | 220 | 198 | 176 | 70 | [1] 72 point Secondary Disconnects were required when the following options are selected on the WavePro breaker: Open Fuse Lockout, Remote Charge Indicator, Shunt Trip 2, 7 Stage Aux Switch, 5000A, EntelliGuard TU w/ RELT This equates to the following selected options on the Retrofill Breaker: Open Fuse Lockout, Charging Motor, Shunt Trip 2, 8 Stage Aux Switch, 5000A, or RELT, Command Close Coil, UV Trip 2, Second Input \ Output, Network Interlock
|  |  | D | Federal Pacific - OEM (FUTURE) |  | 25 | 2500A |  |  |  | Yes | M | 1600A | AL-50 |  | 50 | [6 empty] | - | M | 1200A | [11 empty] | M | 1200A | [11 empty] | M | 1200A | [11 empty] | M | 1200A | [11 empty] | M | 1200A
|  |  | E | Westinghouse - (FUTURE) |  | 30 | 3000A |  | 1 (only) |  |  | N | 1600A | [10 empty] | N | 1600A | 1 | AK-50, AKS-50, AKJ-50 | 65 | 65 | 50 | 65 | 65 | 50 | 65 | 800, 1000, 1200, 1600 | 1600 | N | 1600A | [11 empty] | N | 1600A | [11 empty] | N | 1600A | 1 | WavePro WPS-16 | 65 | 50 | 42 | 50 | 50 | 42 | 50@508V 42@635V | 800, 1600 | 1600 | N | 1600A | EGS-16 | 50 | 50 | 42 | 50 | 50 | 42 | 42/50[7]
|  |  | F | Westinghouse - (FUTURE) |  | 32 | 3200A |  | 2,3,6,7,8 (only) |  | Yes | O | 1600A | [10 empty] | O[1],[3] | 1600A | 1 | AKU-50, AKSU-50 | 100 | 100 | 100 | - | - | - | n/a | 800, 1600 | - | O | 1600A | [11 empty] | O | 1600A | [11 empty] | O | 1600A | [11 empty] | O | 1600A
|  |  | G | Mpact Retrofill -Mpro TU | IEC | 40 | 4000A |  | 1,2,3,6,7,8 (only) |  |  | P | 1600A | [10 empty] | P | 1600A | [11 empty] | P | 1600A | 1 | AKR-50, AKR-50H | 65 | 65 | 50 | 65 | 65 | 50 | 65 | 1000, 1200, 1600 | 1600 | P | 1600A | 1 | AKR-50, AKR-50H | 65 | 65 | 50 | 65 | 65 | 50 | 65 | 1000, 1200, 1600 | 1600 | P | 1600A | 1 | WavePro WPH-16 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 800, 1600 | 1600 | P | 1600A | EGH-16 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | [14 empty] | [2] Not available for Frame Size 40
|  |  | H | GE AKD8 Horizontal Lower Stud [1] | ANSI | 50 | 5000A |  | 3,6,7,8 (only) |  |  | Q | 1600A | [10 empty] | Q | 1600A | [11 empty] | Q | 1600A | 1 | AKRU-50 | 100 | 100 | 100 | - | - | - | n/a | 800, 1600 | - | Q | 1600A | 1 | AKRU-50 | 100 | 100 | 100 | - | - | - | n/a | 800, 1600 | - | Q | 1600A | 1 | WavePro WPF-16 | 100 | 100 | 100 | - | - | - | n/a | 800, 1600 | - | Q | 1600A | EGF-16 | 100 | 100 | 100 | - | - | - | n/a | [14 empty] | [3] AKD6 LF is from 3200A - 4000A
|  |  | I | Mpact Retrofill -GTU | IEC | Notes: | [5 empty] | R | 1600A | AK-50 | 65 | 65 | 50 | 65 | 65 | 50 | 65 | 800, 1600 | - | R | 1600A | [11 empty] | R | 1600A | [11 empty] | R | 1600A | [11 empty] | R | 1600A | [11 empty] | R | 1600A | [22 empty] | [4] AKD6 SF is from upto 2000A
|  |  | J | Mpact Retrofill -Switch | IEC | [1] See Variant for Integrally Fused below | [5 empty] | S | 1600A | AKU-50 | 100 | 100 | 100 | - | - | - | n/a | 800, 1600 | - | S | 1600A | [11 empty] | S | 1600A | [11 empty] | S | 1600A | [11 empty] | S | 1600A | [11 empty] | S | 1600A | [22 empty] | [5] Legacy 24 pin harness supported by ABB Rotterdam (NY)
|  |  | K | ITE - (FUTURE) | [7 empty] | T | 2000A | [10 empty] | T[3] | 2000A | 1 | AKT-50, AKST-50, AKJT-50, AKJT-50H | 65 | 65 | 50 | 65 | 65 | 50 | 65 | 2000 | 2000 | T | 2000A | [11 empty] | T | 2000A | [11 empty] | T | 2000A | 1 | WavePro WPS-20 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2000 | 2000 | T | 2000A | EGS-20 | 65 | 65 | 65 | 65 | 65 | 65 | 65
|  |  | L | ITE - (FUTURE) | [7 empty] | U | 2000A | [10 empty] | U | 2000A | [11 empty] | U | 2000A | 1 | AKRT-50 | 65 | 65 | 50 | 65 | 65 | 50 | 65 | 2000 | 2000 | U | 2000A | 1 | AKRT-50H | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 2000 | 2000 | U | 2000A | [11 empty] | U | 2000A
|  |  | M | ITE OEM - (FUTURE) |  | EntelliGuard R (Retrofill) - Integrally Fused AK/AKR Nomenclature Variant | [5 empty] | V | 2000A | [10 empty] | V[3] | 2000A | [11 empty] | V | 2000A | [11 empty] | V | 2000A | [11 empty] | V | 2000A | [11 empty] | V | 2000A
|  |  | N | Allis Chalmers (FUTURE) | [7 empty] | W | 2000A | AKT-50 | 65 | 65 | 50 | 65 | 65 | 50 | 65 | 2000 | 2000 | W | 2000A | [11 empty] | W | 2000A | [11 empty] | W | 2000A | [11 empty] | W | 2000A | [11 empty] | W | 2000A
|  |  | O | Allis Chalmers (FUTURE) |  | DIGITS 3 |  |  | DIGITS 4 |  |  | X | 3000A | [10 empty] | X | 3000A | 2.5 | AK-75 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 3000 | 3000 | X | 3000A | [11 empty] | X | 3000A | [11 empty] | X | 3000A | [11 empty] | X | ALL | EGF-XX | 200 | 200 | 200 | 200 | 200 | 200 | -
|  |  | P | Allis Chalmers (FUTURE) |  | SENSOR SIZE |  |  | FUSE SIZE |  |  | Y | 3000A | [10 empty] | Y | 3000A | [11 empty] | Y | 3000A | [11 empty] | Y | 3000A | [11 empty] | Y | 3000A | [11 empty] | Y | 3000A
|  |  | Q | Allis Chalmers OEM (FUTURE) |  | Character | Description |  | Character | Description | Fuse Details | Z | 3000A | [10 empty] | Z | 3000A | [11 empty] | Z | 3000A | [11 empty] | Z | 3000A | [11 empty] | Z | 3000A | [11 empty] | Z | 3000A
|  |  | R | ME07 | IEC | A | 150 |  | 0 | 250 | 1Hole Tangs | 1 | 3200A | [10 empty] | 1 | 3200A | [11 empty] | 1 | 3200A | 2.5 | AKR-75 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 3200 | 3200 | 1 | 3200A | 2.5 | AKR-75 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 3200 | 3200 | 1 | 3200A | 2.5 | WPS-32 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 3200 | 3200 | 1 | 3200A | EGS-32 | 65 | 65 | 65 | 65 | 65 | 65 | 65
|  |  | S | ABB (FUTURE) |  | B | 200 |  | 1 | 300 |  | 2 | 3200A | [10 empty] | 2 | 3200A | [11 empty] | 2 | 3200A | [11 empty] | 2 | 3200A | 2.5 | AKR-75H | 130 | 85 | 85 | 85 | 85 | 85 | 85 | 3200 | 3200 | 2 | 3200A | 2.5 | WPH-32 | 130 | 85 | 85 | 85 | 85 | 85 | 85 | 3200 | 3200 | 2 | 3200A | EGH-32 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  | T | ABB (FUTURE) |  | C | 225 |  | 2 | 350 |  | 3 | 3200A | [10 empty] | 3 | 3200A | [11 empty] | 3 | 3200A | [11 empty] | 3 | 3200A | [11 empty] | 3 | 3200A | 2.5 | WPX-32 | 130 | 100 | 85 | 100 | 100 | 85 | 100 | 3200 | 3200 | 3 | 3200A | EGX-32 | 100 | 100 | 85 | 100 | 100 | 85 | 100/85[7]
|  |  | U | Schneider (FUTURE) |  | D | 400 |  | 3 | 400 |  | 4 | 3200A | [10 empty] | 4 | 3200A | [11 empty] | 4 | 3200A | [11 empty] | 4 | 3200A | [11 empty] | 4 | 3200A | [11 empty] | 4 | 3200A
|  |  | V | Schneider (FUTURE) |  | E | 600 |  | 4 | 450 |  | 5 | 4000A | [10 empty] | 5 | 4000A | 2.5 | AK-100 | 130 | 85 | 85 | 85 | 85 | 85 | 85 | 4000 | 4000 | 5 | 4000A | 2.5 | AKR-100 | 130 | 85 | 85 | 85 | 85 | 85 | 85 | 4000 | 4000 | 5 | 4000A | 2.5 | AKR-100 | 130 | 85 | 85 | 85 | 85 | 85 | 85 | 4000 | 4000 | 5 | 4000A | 2.5 | WPS-40 | 130 | 85 | 85 | 85 | 85 | 85 | 85 | 4000 | 4000 | 5 | 4000A | EGS-40 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  | W | Schneider (FUTURE) |  | F | 800 |  | 5 | 500 |  | 6 | 4000A | [10 empty] | 6 | 4000A | [11 empty] | 6 | 4000A | [11 empty] | 6 | 4000A | [11 empty] | 6 | 4000A | 2.5 | WPX-40 | 130 | 100 | 85 | 100 | 100 | 85 | 100 | 4000 | 4000 | 6 | 4000A | EGX-40 | 100 | 100 | 85 | 100 | 100 | 85 | 100
|  |  | X | FUTURE |  | G | 1200 |  | 6 | 600 |  | 7 | 4000A | [10 empty] | 7 | 4000A | [11 empty] | 7 | 4000A | [11 empty] | 7 | 4000A | [11 empty] | 7 | 4000A | [11 empty] | 7 | 4000A | [7 empty] | 100/85[7]
|  |  | Y | FUTURE |  | H | 1600 |  | 7 | 601 | 1 Hole Tangs w/ Large fuse body | 8 | 5000A | [10 empty] | 8 | 5000A | [11 empty] | 8 | 5000A | [11 empty] | 8 | 5000A | 3 | AKR-125 | 130 | 85 | 85 | 85 | 85 | 85 | 85 | 5000 | 5000 | 8 | 5000A | 3 | WPS-50 | 130 | 85 | 85 | 85 | 85 | 85 | 85 | 5000 | 5000 | 8 | 4000A
|  |  | Z | FUTURE |  | J | 2000 |  | 8 | 650 |  | 9 | 5000A | [10 empty] | 9 | 5000A | [11 empty] | 9 | 5000A | [11 empty] | 9 | 5000A | [11 empty] | 9 | 5000A | 3 | WPX-50 | 130 | 100 | 85 | 100 | 100 | 85 | 100 | 5000 | 5000 | 9 | 5000A | EGS-50 | 85 | 85 | 85 | 85 | 85 | 85 | 85
|  |  | Notes: |  |  | K | 2500 |  | 9 | 700 |  | 0 | 5000A | [10 empty] | 0 | 5000A | [11 empty] | 0 | 5000A | [11 empty] | 0 | 5000A | [11 empty] | 0 | 5000A | [11 empty] | 0 | 5000A | EGX-50 | 100 | 100 | 85 | 100 | 100 | 85 | 100/85[7]
|  |  | [1] • ALL Breakers (OEM & GE) had Horizontal Upper Studs • OEM AKD8 breakers always had Horizontal Lower Studs • GE Mod 1 had Vertical Lower Studs for Feeders (Feeders = Connected to Runbacks, not Risers) • GE Mod 1 had Horizontal Lower Studs for 2000A and below Main and Tie Breakers (Main \ Tie = Connected to Riser, no Runbacks) • GE Mod 1 had Vertical Lower Studs for greater than 2000A Mains and Tie Breakers • GE Mod 2 and Mod 3 have Vertical Lower Studs on Mains, Ties and Feeders • Impossible to tell by looking at the GE Equipment summary if the equipment is Mod 1 or Mod 2 or Mod 3 • Mod 1 started into production around 1980 and continued several years. It was produced at the same time as Mod 2 • Mod 2 started into production around 1982 and was produced at the same time as Mod 3 • Mod 3 start into production around 1990 |  |  | L | 3000 |  | A | 750 |  | Notes:
[6 empty] | M | 3200 |  | B | 800 |  |  | [1] Non-Standard Construction. Not UL Listed
[6 empty] | N | 4000 |  | C | 801 | 2 Hole Tang |  | [2] Non-Standard Construction. UL Listed
[6 empty] | P | 5000 |  | D | 900 |  |  | [3] Planned Release
[6 empty] | Q | 6000 |  | E | 1000 |  |  | [4] See table below for UL approved combinations
[6 empty] | X | Switch |  | F | 1100 |  |  | [5] 2nd Value for 4th Pole
[9 empty] | G | 1200 |  |  | [6] 2nd Value for Drawout Breaker
[9 empty] | H | 1201 | 2 Hole Tang w/ medium fuse body |  | [7] 2nd Value for 635V
[9 empty] | I | 1350
[9 empty] | J | 1400
[9 empty] | K | 1500
[9 empty] | L | 1600 |  | UL Approved Combinations
[9 empty] | M | 1601 | 2 Hole Tang w/ large fuse body | Breaker Type | Cat. No. | Frame size | Continuous Current Rating
[9 empty] | N | 1800 |  | AKD5-AK25-600A CAT. NOS (Fig. 1) | R106D | 600 | 600
[9 empty] | O | 2000 |  |  | R104D | 600 | 400
[9 empty] | P | 2001 | 4 Hole Tang |  | R406D | 600 | 600
[9 empty] | Q | 2200 |  |  | R404D | 600 | 400
[9 empty] | R | 2500 |  | AKD5-AK50/AKS50-1600A CAT. NOS. (Fig. 2) | R116N | 1600 | 1600
[9 empty] | S | 3000 |  |  | R112N | 1600 | 1200
[9 empty] | T | 3001 | 4 Hole Tang, Diff. Hole Pattern |  | R110N | 1600 | 1000
[9 empty] | U | 208 V | OFLO ONLY |  | R108N | 1600 | 800
[9 empty] | V | 240 V | OFLO ONLY |  | R416N | 1600 | 1600
[9 empty] | W | 480 V | OFLO ONLY |  | R412N | 1600 | 1200
[9 empty] | X | 600 V | OFLO ONLY |  | R410N | 1600 | 1000
[9 empty] | Y | 380 V/50 Hz | OFLO ONLY |  | R408N | 1600 | 800
[9 empty] | Z | 415 V/50 Hz | OFLO ONLY | AKD6-AK25-600A CAT. NOS. (Fig. 1) | R206D | 600 | 600
[13 empty] | R204D | 600 | 400
[6 empty] | EntelliGuard RE (Retrofill Entellisys) - Integrally Fused Nomenclature Variant | [6 empty] | R506D | 600 | 600
[6 empty] | (Only 8 digit Configuration) | [6 empty] | R504D | 600 | 400
[6 empty] | DIGITS 3 |  |  | DIGITS 4 |  |  | AKD6-AK50/AKS50-1600A CAT. NOS. (Fig. 2) | R216N | 1600 | 1600
[6 empty] | SWITCH FRAME SIZE (Legacy 4th Digit) |  |  | FUSE SIZE (Legacy 3rd Digit) |  |  |  | R212N | 1600 | 1200
[6 empty] | Character | Description |  | Character | Fuse Rating (A) | Fuse Details |  | R210N | 1600 | 1000
[6 empty] | A | 150 |  | 4 | None (OFLO Only) | None |  | R208N | 1600 | 800
[6 empty] | E | 200 |  | A | 300 | Class J |  | R516N | 1600 | 1600
[6 empty] | H | 225 |  | B | 350 | Class J |  | R512N | 1600 | 1200
[6 empty] | K | 400 |  | C | 400 | Class J |  | R510N | 1600 | 1000
[6 empty] | M | 600 |  | D | 450 | Class J |  | R508N | 1600 | 800
[6 empty] | P | 800 |  | E | 500 | Class J | AKD6-AKR30/AKR30H-800A CAT. NOS (Fig. 3) | R208G | 800 | 800
[9 empty] | F | 600 | Class J |  | R206G | 800 | 600
[9 empty] | G | 800 | Class L |  | R204G | 800 | 400
[9 empty] | H | 1000 | Class L |  | R508G | 800 | 800
[9 empty] | J | 1200 | Class L |  | R506G | 800 | 600
[9 empty] | K | 1600 | Class L |  | R504G | 800 | 400
[9 empty] | L | 2000 | Class L | AKD6-AKR50/AKR50H-1600A CAT. NOS (Fig. 3) | R216P | 1600 | 1600
[9 empty] | M | 2500 | Class L (Silver Fuse) |  | R212P | 1600 | 1200
[9 empty] | N | 800 | Welder Limiter |  | R210P | 1600 | 1000
[9 empty] | Q | 1600 | Welder Limiter |  | R516P | 1600 | 1600
[9 empty] | R | 2000 | Welder Limiter |  | R512P | 1600 | 1200
[13 empty] | R510P | 1600 | 1000
[12 empty] | AKD8-AKR30/AKR30H-800A CAT. NOS. (Fig. 4) | R308G | 800 | 800
[13 empty] | R306G | 800 | 600
[13 empty] | R304G | 800 | 400
[13 empty] | R608G | 800 | 800
[13 empty] | R606G | 800 | 600
[13 empty] | R604G | 800 | 400
[12 empty] | AKD8-AKR30L-800A CAT. NOS. (Fig. 4) | R308I | 800 | 800
[13 empty] | R306I | 800 | 600
[13 empty] | R304I | 800 | 400
[13 empty] | R608I | 800 | 800
[13 empty] | R606I | 800 | 600
[13 empty] | R604I | 800 | 400
[12 empty] | AKD8-AKR30S-800A CAT. NOS. (Fig. 5) | R308J | 800 | 800
[13 empty] | R306J | 800 | 600
[13 empty] | R304J | 800 | 400
[13 empty] | R608J | 800 | 800
[13 empty] | R606J | 800 | 600
[13 empty] | R604J | 800 | 400
[12 empty] | AKD8-AKR50/AKR50H-1600A CAT. NOS. (Fig. 4) | R316P | 1600 | 1600
[13 empty] | R312P | 1600 | 1200
[13 empty] | R310P | 1600 | 1000
[13 empty] | R616P | 1600 | 1600
[13 empty] | R612P | 1600 | 1200
[13 empty] | R610P | 1600 | 1000
[12 empty] | AKD5-AK25-600A (Fig. 1) | R1XXD | 600 | 600
[13 empty] | R4XXD | 600 | 600
[12 empty] | AKD5-AK50/AK5S50-1600A (Fig.2) | R1XXN | 1600 | 1600
[13 empty] | R4XXN | 1600 | 1600
[12 empty] | AKD6-AK25-600A (Fig. 1) | R2XXD | 600 | 600
[13 empty] | R5XXD | 600 | 600
[12 empty] | AKD6-AK50/AKS50-1600A (Fig. 2) | R2XXN | 1600 | 1600
[13 empty] | R5XXN | 1600 | 1600
[12 empty] | AKD6-AKR30/AKR30H-800A (Fig.3) | R2XXG | 800 | 800
[13 empty] | R5XXG | 800 | 800
[12 empty] | AKD6-AKR50/AKR50H-1600A (Fig. 3) | R2XXP | 1600 | 1600
[13 empty] | R5XXP | 1600 | 1600
[12 empty] | AKD8-AKR30/AKR30H-800A (Fig. 4) | R3XXG | 800 | 800
[13 empty] | R6XXG | 800 | 800
[12 empty] | AKD8-AKR30L-800A (Fig.4) | R3XXI | 800 | 800
[13 empty] | R6XXI | 800 | 800
[12 empty] | AKD8-AKR30S-800A (Fig. 5) | R3XXJ | 800 | 800
[13 empty] | R6XXJ | 800 | 800
[12 empty] | AKD8-AKR50/AKR50H-1600A (Fig. 4) | R3XXP | 1600 | 1600
[13 empty] | R6XXP | 1600 | 1600
Preliminary

## M-Pact Retrofill Variant
Home
EntelliGuard R (Retrofill) Nomenclature Variant
| DIGIT 1 |  | DIGIT 2 |  |  | M Pact Retrofill DIGITS 3, 4 |  |  |  | M Pact Retrofill DIGITS 5, 6 | [20 empty] | DIGIT 6 |  |  | Continue…
| PRODUCT LINE DEFINITION |  | PRODUCT TYPE |  | Electrical Standards | CURRENT RATING |  |  |  | Character | Breaker | [9 empty] | Non-Auto CB/Switch | [9 empty] | CONSTRUCTION
| Character | Description | Character | Description |  | Character | Description | Breakers | Non-Auto CB/Switch |  | Type LG or LI | [9 empty] | Type LJ | [9 empty] | Character | Description | EGL | Same Nomenclature is follows from 7-20 Digit
[8 empty] | EGL | EGL |  | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A
| R | EntelliGuard R Breaker & Switch [1] | 1 | GE AKD5, GE AKD6 (AK25 and AK50 Only) | ANSI |  |  | IEC | IEC | [21 empty] | 1 | OEM Drawout - 3 Pole | Yes
| Notes: |  | 2 | GE AKD6 | ANSI | 4 | 400A | Yes | Yes | [21 empty] | 2 | OEM Drawout - 4 Pole, right | Yes
|  | [1] Drawout Construction only | 3 | GE AKD8 Vertical Lower Stud [1] | ANSI |  |  |  |  | R[13] | [10 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 3 | OEM Drawout - 4 Pole, left | Yes
|  |  | 4 | OEM, AKD5 and AKD6 AK25, AK50 | ANSI | 7 | 630A | Yes | Yes | S | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [12 empty] | 4 | OEM Stationary - 3 Pole | Yes
|  |  | 5 | OEM, AKD6 | ANSI | 8 | 800A | Yes | Yes | C | [6 empty] | 2 | 2 | 2 | 2 | [6 empty] | 2 | 2 | 2 | 2 | 5 | OEM Stationary - 4 Pole, right | Yes
|  |  | 6 | OEM AKD8 Horizontal Lower Stud [1] | ANSI | 10 | 1000A | Yes | Yes | K | [20 empty] | 6 | OEM Stationary - 4 Pole, left | Yes
|  |  | 7 | GE AKD10 | ANSI |  |  |  |  | F | [20 empty] | 7
|  |  | 8 | GE OEM, AKD10 | ANSI | 13 | 1250A | Yes | Yes | N | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [12 empty] | 8
|  |  | 9 | GE, AKD10 Entellisys | ANSI | 16 | 1600A | Yes | Yes | D | [6 empty] | 2 | 2 | 2 | 2 | [10 empty] | 9
|  |  | 0 | GE AKD | ANSI, Not Listed | 20 | 2000A | Yes | Yes | H | [20 empty] | 0
|  |  | A | Federal Pacific (FUTURE) |  | 25 | 2500A | Yes | Yes | P | [20 empty] | A | GE Wind Stationary - 3 Pole [4]
|  |  | B | Federal Pacific (FUTURE) | [5 empty] | E | [20 empty] | B | GE Wind Stationary - 4 Pole, left [4]
|  |  | C | Federal Pacific (FUTURE) |  | 32 | 3200A | Yes | Yes | M | [20 empty] | C | GE Wind Stationary - 4 Pole, right [4]
|  |  | D | Federal Pacific - OEM (FUTURE) |  | 40 | 4000A | Yes | Yes | B | [20 empty] | D | GE Drawout - 3 Pole
|  |  | E | Westinghouse - (FUTURE) | [5 empty] | G | [20 empty] | E
|  |  | F | Westinghouse - (FUTURE) | [5 empty] | L | [20 empty] | F | GE Stationary - 3 Pole
|  |  | G | Mpact Retrofill -Mpro TU | IEC |  |  |  |  | U | [20 empty] | G
|  |  | H | GE AKD8 Horizontal Lower Stud [1] | ANSI |  |  |  |  | V | [20 empty] | H
|  |  | I | Mpact Retrofill -GTU | IEC |  |  |  |  | W | [20 empty] | I
|  |  | J | Mpact Retrofill -Switch | IEC |  |  |  |  | T[17] | [20 empty] | J
|  |  | K | ITE - (FUTURE) | [26 empty] | K
|  |  | L | ITE - (FUTURE) | [26 empty] | L | GE Drawout - 4 Pole, left (future)
|  |  | M | ITE OEM - (FUTURE) | [26 empty] | M
|  |  | N | Allis Chalmers (FUTURE) | [26 empty] | N
|  |  | O | Allis Chalmers (FUTURE) | [26 empty] | O
|  |  | P | Allis Chalmers (FUTURE) | [26 empty] | P
|  |  | Q | Allis Chalmers OEM (FUTURE) | [26 empty] | Q
|  |  | R | ME07 | IEC | [25 empty] | R | GE Drawout - 4 Pole, right (future)
|  |  | S | ABB (FUTURE) | [26 empty] | S | GE Drawout - 3 Pole Single Cluster [1]
|  |  | T | ABB (FUTURE) | [26 empty] | T
|  |  | U | Schneider (FUTURE) | [26 empty] | U
|  |  | V | Schneider (FUTURE) | [26 empty] | V | GE Stationary - 4 Pole, right
|  |  | W | Schneider (FUTURE) | [26 empty] | W | GE Stationary - 4 Pole, left
|  |  | X | FUTURE | [26 empty] | X | OEM Stationary - 3 Pole, No Rear Terminations
|  |  | Y | FUTURE | [26 empty] | Y | OEM Stationary - 4 Pole, Right, No Rear Terminations
|  |  | Z | FUTURE | [26 empty] | Z | OEM Stationary - 4 Pole, Left, No Rear Terminations
|  |  | Notes: | [27 empty] | Notes:
[1] • ALL Breakers (OEM & GE) had Horizontal Upper Studs • OEM AKD8 breakers always had Horizontal Lower Studs • GE Mod 1 had Vertical Lower Studs for Feeders (Feeders = Connected to Runbacks, not Risers) • GE Mod 1 had Horizontal Lower Studs for 2000A and below Main and Tie Breakers (Main \ Tie = Connected to Riser, no Runbacks) • GE Mod 1 had Vertical Lower Studs for greater than 2000A Mains and Tie Breakers • GE Mod 2 and Mod 3 have Vertical Lower Studs on Mains, Ties and Feeders • Impossible to tell by looking at the GE Equipment summary if the equipment is Mod 1 or Mod 2 or Mod 3 • Mod 1 started into production around 1980 and continued several years. It was produced at the same time as Mod 2 • Mod 2 started into production around 1982 and was produced at the same time as Mod 3 • Mod 3 start into production around 1990

## Retrofill Cassette Variant
Home
EntelliGuard R (Retrofill) Nomenclature Variant
| DIGIT 1 |  | DIGIT 2 |  | DIGITS 3, 4 |  | DIGIT 5 | [54 empty] | DIGIT 6 |  | Cassette Type Availability | Complete Retrofill Cassette Cat #
| PRODUCT LINE DEFINITION |  | PRODUCT TYPE |  | CURRENT RATING |  | CONSTRUCTION | [54 empty] | SECONDARY DISCONNECT CONSTRUCTION
| Character | Description | Character | Description | Character | Description | Digit 2 = 0 | [9 empty] | Digit 2 = 1, 4 | [9 empty] | Digit 2 = 2,5 | [9 empty] | Digit 2 = 3,6 | [9 empty] | Digit 2 = 7,8 | [14 empty] | Character | Description
[7 empty] | Character | Frame Size | GE AKD | AIC w/Inst. (kA) |  |  | AIC w/o Inst. (kA) |  |  | Icw w/ Inst. | Character | Frame Size | GE/OEM AKD5 and AKD6 AK25, AK50 | AIC w/Inst. (kA) |  |  | AIC w/o Inst. (kA) |  |  | Icw w/ Inst. | Character | Frame Size | GE/OEM AKD6 | AIC w/Inst. (kA) |  |  | AIC w/o Inst. (kA) |  |  | Icw w/ Inst. | Character | Frame Size | GE/OEM AKD8 | AIC w/Inst. (kA) |  |  | AIC w/o Inst. (kA) |  |  | Icw w/ Inst. | Character | Frame Size | GE/OEM AKD10 | AIC w/Inst. (kA) |  |  | AIC w/o Inst. (kA) |  |  | Icw (kA) w/ Inst. | A-D | E-I | J-M | N-Q | R-Z
| R | EntelliGuard R Breaker & Switch | 1 | GE AKD5 and GE AKD6 AK25,AK50 | XX | No Sensor (Switch) |  |  | Breaker Type | 254V | 508V | 635V | 254V | 508V | 635V |  |  |  | Breaker Type | 254V | 508V | 635V | 254V | 508V | 635V |  |  |  | Breaker Type | 254V | 508V | 635V | 254V | 508V | 635V |  |  |  | Breaker Type | 254V | 508V | 635V | 254V | 508V | 635V |  |  |  | Breaker Type | 254V | 508V | 635V | 254V | 508V | 635V |  | Fed Pacific | Westinghouse | ITE | Allis | Future | 1 | No Sec Disc Bullet or Harnesses | All
|  |  | 2 | GE AKD6 | 01 | 150A (Future) | A | 225A | [8 empty] | A | 225A | AK-1-15 | [7 empty] | A | 225A | N/A | [7 empty] | A | 225A | N/A | [7 empty] | A | 225A | N/A | [8 empty] | DB-15 | KA |  |  | 2 | A,B,C Bullet Disc Installed | AK50/50H, AKT50/50H, AKST50/50H, AKJT50/50H, AK75, AK100, AKR75, AKR100 Only
|  |  | 3 | GE AKD8 | 02 | 200A | B[1] | 225A | AK-15 | ? | ? | ? | ? | ? | ? | ? | B | 225A | [8 empty] | B | 225A | [8 empty] | B | 225A | [8 empty] | B | 225A | [9 empty] | DK-15 | KA-225 |  |  | 3 | A,B,C,D Bullet Disc Installed | AK-25 Only
|  |  | 4 | GE OEM, AKD5 and AKD6 AK25, AK50 Version Cassette | 03 | 225A | C | 600A | [8 empty] | C | 600A | [8 empty] | C | 600A | [8 empty] | C | 600A | [8 empty] | C | 600A | [9 empty] | DB-25 | KB | LA-25, LA25A |  | 4 | A,B,C Bullet Disc Installed & 19 Pin Programmer Harness | AKR-75,AKR-100
|  |  | 5 | GE OEM, AKD6 Version Cassette | 04 | 400A | D | 600A | [8 empty] | D | 600A | AK-25 | 42 | 42 | 42 | 22 | 22 | 22 | 22 | D | 600A | [8 empty] | D | 600A | [8 empty] | D | 600A | [9 empty] | DBL-25 | K-600 | LA-600, LAF-600 (Blue)
|  |  | 6 | GE OEM, AKD8 Version Cassette | 06 | 600A | E | 600A | [8 empty] | E[1],[3] | 600A | AKU-25 | ? | ? | ? | ? | ? | ? | ? | E | 600A | [8 empty] | E | 600A | [8 empty] | E | 600A | [9 empty] | DK-25 | KDON-600 | LA-600, LAF-600 (Gold)
|  |  | 7 | GE AKD10 | 08 | 800A | F | 600A | [8 empty] | F | 600A | [8 empty] | F | 600A | [8 empty] | F | 600A | [8 empty] | F | 600A
|  |  | 8 | GE OEM, AKD10 | 10 | 1000A | G | 800A | [8 empty] | G | 800A | [8 empty] | G | 800A | [8 empty] | G | 800A | [8 empty] | G | 800A | [9 empty] | DS-206, DSL206 | KC-800 | LA-50
|  |  | 9 | GE (Future, IEC?) | 12 | 1200A | H | 800A | [8 empty] | H | 800A | [8 empty] | H | 800A | [8 empty] | H | 800A | [8 empty] | H | 800A | [10 empty] | K-800 | LA-800, LAF-800
|  |  | 0 | GE AKD | 16 | 1600A | I | 800A | [8 empty] | I | 800A | [8 empty] | I | 800A | [8 empty] | I | 800A | [8 empty] | I | 800A | [10 empty] | KDON-800 | RL-800, RLX-800, RLE-800
|  |  | A | Federal Pacific (FUTURE) | 20 | 2000A | J | 800A | [8 empty] | J | 800A | [8 empty] | J | 800A | [8 empty] | J | 800A | [8 empty] | J | 800A
|  |  | B | Federal Pacific (FUTURE) | 25 | 2500A (Future) | K | 800A | [8 empty] | K | 800A | [8 empty] | K | 800A | [8 empty] | K | 800A | [8 empty] | K | 800A
|  |  | C | Federal Pacific (FUTURE) | 30 | 3000A | L | 800A | [8 empty] | L | 800A | [8 empty] | L | 800A | [8 empty] | L | 800A | [8 empty] | L | 800A
|  |  | D | Federal Pacific - OEM (FUTURE) | 32 | 3200A | M | 1200A | [8 empty] | M | 1200A | [8 empty] | M | 1200A | [8 empty] | M | 1200A | [8 empty] | M | 1200A
|  |  | E | Westinghouse - (FUTURE) | 40 | 4000A | N | 1600A | [8 empty] | N | 1600A | AK-50, AKS-50 | 65 | 65 | 50 | 65 | 65 | 50 | 65 | N | 1600A | [8 empty] | N | 1600A | [8 empty] | N | 1600A
|  |  | F | Westinghouse - (FUTURE) | 50 | 5000A (Future) | O | 1600A | [8 empty] | O[1],[3] | 1600A | AKU-50, AKSU-50 | ? | ? | ? | ? | ? | ? | ? | O | 1600A | [8 empty] | O | 1600A | [8 empty] | O | 1600A
|  |  | G | Mpact Retrofill -Mpro TU |  |  | P | 1600A | [8 empty] | P | 1600A | [8 empty] | P | 1600A | [8 empty] | P | 1600A | [8 empty] | P | 1600A
|  |  | H | GE AKD8 Horizontal Lower Stud [1] |  |  | Q | 1600A | [8 empty] | Q | 1600A | [8 empty] | Q | 1600A | [8 empty] | Q | 1600A | [8 empty] | Q | 1600A
|  |  | I | Mpact Retrofill -GTU |  |  | R | 1600A | [8 empty] | R | 1600A | [8 empty] | R | 1600A | [8 empty] | R | 1600A | [8 empty] | R | 1600A
|  |  | J | Mpact Retrofill -Switch |  |  | S | 1600A | [8 empty] | S | 1600A | [8 empty] | S | 1600A | [8 empty] | S | 1600A | [8 empty] | S | 1600A
|  |  | K | ITE - (FUTURE) |  |  | T | 2000A | [8 empty] | T[3] | 2000A | AKT-50, AKST-50 | 42 | 50 | 65 | 42 | 50 | 50 | 42 | T | 2000A | [8 empty] | T | 2000A | [8 empty] | T | 2000A
|  |  | L | ITE - (FUTURE) |  |  | U | 2000A | [8 empty] | U | 2000A | [8 empty] | U | 2000A | [8 empty] | U | 2000A | [8 empty] | U | 2000A
|  |  | M | ITE OEM - (FUTURE) |  |  | V | 2000A | [8 empty] | V[3] | 2000A | AKJT-50, AKJT-50H | 42 | 50 | 65 | 42 | 50 | 50 | 42 | V | 2000A | [8 empty] | V | 2000A | [8 empty] | V | 2000A
|  |  | N | Allis Chalmers (FUTURE) |  |  | W | 2000A | [8 empty] | W | 2000A | [8 empty] | W | 2000A | [8 empty] | W | 2000A | [8 empty] | W | 2000A
|  |  | O | Allis Chalmers (FUTURE) |  |  | X | 3000A | [8 empty] | X[4] | 3000A | AK-75 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | X | 3000A | [8 empty] | X | 3000A | [8 empty] | X | 3000A
|  |  | P | Allis Chalmers (FUTURE) |  |  | Y | 3000A | [8 empty] | Y | 3000A | [8 empty] | Y | 3000A | [8 empty] | Y | 3000A | [8 empty] | Y | 3000A
|  |  | Q | Allis Chalmers OEM (FUTURE) |  |  | Z | 3000A | [8 empty] | Z | 3000A | [8 empty] | Z | 3000A | [8 empty] | Z | 3000A | [8 empty] | Z | 3000A
|  |  | R | ME07 |  |  | 1 | 3200A | [8 empty] | 1 | 3200A | [8 empty] | 1 | 3200A | AKR-75 | 85 | 65 | 65 | 65 | 65 | 65 | 65 | 1 | 3200A | [8 empty] | 1 | 3200A
|  |  | S | ABB (FUTURE) |  |  | 2 | 3200A | [8 empty] | 2 | 3200A | [8 empty] | 2 | 3200A | [8 empty] | 2 | 3200A | [8 empty] | 2 | 3200A
|  |  | T | ABB (FUTURE) |  |  | 3 | 3200A | [8 empty] | 3 | 3200A | [8 empty] | 3 | 3200A | [8 empty] | 3 | 3200A | [8 empty] | 3 | 3200A
|  |  | U | Schneider (FUTURE) |  |  | 4 | 3200A | [8 empty] | 4 | 3200A | [8 empty] | 4 | 3200A | [8 empty] | 4 | 3200A | [8 empty] | 4 | 3200A
|  |  | V | Schneider (FUTURE) |  |  | 5 | 4000A | [8 empty] | 5(4) | 4000A | AK-100 | 130 | 85 | 85 | 85 | 85 | 85 | 85 | 5 | 4000A | AKR-100 | 130 | 85 | 85 | 85 | 85 | 85 | 85 | 5 | 4000A | [8 empty] | 5 | 4000A
|  |  | W | Schneider (FUTURE) |  |  | 6 | 4000A | [8 empty] | 6 | 4000A | [8 empty] | 6 | 4000A | [8 empty] | 6 | 4000A | [8 empty] | 6 | 4000A
|  |  | X | FUTURE |  |  | 7 | 4000A | [8 empty] | 7 | 4000A | [8 empty] | 7 | 4000A | [8 empty] | 7 | 4000A | [8 empty] | 7 | 4000A
|  |  | Y | FUTURE |  |  | 8 | 4000A | [8 empty] | 8 | 4000A | [8 empty] | 8 | 4000A | [8 empty] | 8 | 4000A | [8 empty] | 8 | 4000A
|  |  | Z | FUTURE |  |  | 9 | 5000A | [8 empty] | 9 | 5000A | [8 empty] | 9 | 5000A | [8 empty] | 9 | 5000A | [8 empty] | 9 | 5000A
[7 empty] | 0 | 5000A | [8 empty] | 0 | 5000A | [8 empty] | 0 | 5000A | [8 empty] | 0 | 5000A | [8 empty] | 0 | 5000A
Notes:
[1] Non-Standard Construction. Not UL Listed
[2] Non-Standard Construction. UL Listed
[3] Planned Release
[4] Only for char 2 = 1, Not for char 2=4
Future

## Entellisys Retrofill Variant
EntelliGuard R (Retrofill) for Entellisys Nomenclature Variant
| DIGIT 1 |  | DIGIT 2,3 |  | DIGIT 4 |  | DIGIT 5 |  | DIGIT 6 |  | DIGIT 7 |  | DIGIT 8
| PRODUCT LINE DEFINITION |  | PRODUCT TYPE |  | INTERRUPTING CAPABILITY/FUSE TYPE |  | FRAME SIZE |  | OPERATION |  | ACCESSORY |  | SUFFIX
| Character | Description | Character | Description | Character | Description | Character | Description | Character | Description | Character | Description | Character | Description
| R | EntelliGuard R | EG | EntelliGuard (WavePro Style Entellisys) Breaker | 1 | Standard (EGS) | A | 800A | X | Manual | X | None | X | Unused
[5 empty] | 2 | High (EGH) | E | 1600A | 1 | Electrically Operated (120Vac Charge, Close, Trip) | B | Bell Alarm w/Lockout
[5 empty] | 3 | Extended (EGX) | H | 2000A |  |  | N | Network Interlock (Includes Hidden On Button), E/O Only
[5 empty] | 4 | OFLO Only - 240V - 480V System Voltage | K | 3200A
[5 empty] | 5 | OFLO Only - 480V System Voltage | M | 4000A
[5 empty] | 6 | OFLO Only - 600V System Voltage | P | 5000A
[5 empty] | 7 | OFLO Only - 208V System Voltage
[5 empty] | 8 | OFLO Only - 380V 50 Hz System Voltage
[5 empty] | 9 | OFLO Only - 415V 50 Hz System Voltage
Fuses for EGF-08/16
[5 empty] | A | 300A Class J Fuse
[5 empty] | B | 350A Class J Fuse
[5 empty] | C | 400A Class J Fuse
[5 empty] | D | 450A Class J Fuse
[5 empty] | E | 500A Class J Fuse
[5 empty] | F | 600A Class J Fuse
[5 empty] | G | 800A Class L Fuse
[5 empty] | H | 1000A Class L Fuse
[5 empty] | J | 1200A Class L Fuse
[5 empty] | K | 1600A Class L Fuse
[5 empty] | L | 2000A Class L Fuse
[5 empty] | M | 2500A Class L Fuse (Silver Fuse)
[5 empty] | N | 800A Welder Limiter
[5 empty] | Q | 1600A Welder Limiter
[5 empty] | R | 2000A Welder Limiter

## AEG (ME10) Variant
Home
AEG Branded EntelliGuard G (ME10) Variant
| DIGIT 1 |  | DIGIT 2 | [6 empty] | DIGITS 3, 4 | [11 empty] | DIGIT 5 | [59 empty] | DIGIT 6 |  |  |  | Continue…
| PRODUCT LINE DEFINITION |  | PRODUCT TYPE | [6 empty] | CURRENT RATING | [11 empty] | INTERRUPTION TIER (kA) and Frame Size | [59 empty] | CONSTRUCTION
| Character | Description | Character | Description | EntelliGuard G |  |  | EGL | EGT | Character | Description | Breakers |  |  |  |  | Non-Auto CB/Switch |  |  |  |  | EntelliGuard G | [47 empty] | EntelliGuard T | [11 empty] | Character | Description | EGG | EGT
[5 empty] | UL | ANSI | IEC | IEC | IEC |  |  | EntelliGuard G |  |  | EGL | EGT | EntelliGuard G |  |  | EGL | EGT | IEC | [61 empty] | IEC
| 1 |  | 1 | [8 empty] | UL | ANSI | IEC |  |  | UL | ANSI | IEC |  |  | Character | Interruption Ratings | [10 empty] | Envelope Size by Rated Current | [47 empty] | 1 | OEM Drawout - 3 Pole | Yes | Yes
| 2 |  | 2 | [6 empty] | 4 | 400A |  |  | Yes |  | Yes |  |  | Yes |  | Yes |  | Icm (kA) peak Isolator | Icm (kA) peak Breaker | Icu (kA) @ 230, 240, 400, 415, 440Vac | Icu (kA) @ 500Vac | Icu (kA) @ 690Vac | Ics (kA) % of Icu | Icw (kA) @ 230-500V | Icw (kA) @ 690V | Icw (kA) @ 250Vdc, 1 pole [4] | Icw (kA) @ 500Vdc, 2 poles [4] | Icw (kA) @ 750Vdc, 3 poles Ϯ | Breaker | [11 empty] | Non-Auto CB/Switch | [11 empty] | Non-Auto CB/Switch w/MCR | [11 empty] | Breaker | [5 empty] | Non-Auto CB/Switch | [5 empty] | 2 | OEM Drawout - 4 Pole, right
| 3 |  | 3 | [6 empty] | 6 | 600A | [22 empty] | Type AG | [11 empty] | Type AJ | [11 empty] | Type AW | [11 empty] | Type AT | [5 empty] | Type A7 | [5 empty] | 3 | OEM Drawout - 4 Pole, left | Yes | Yes
| 4 |  | 4 | [6 empty] | 7 | 630A |  |  | Yes |  | Yes |  |  | Yes |  | Yes | [12 empty] | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 6400A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 6400A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 6400A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 400A | 630A | 800A | 1000A | 1250A | 1600A | 4 | OEM Stationary - 3 Pole | Yes | Yes
| 5 |  | 5 | [6 empty] | 8 | 800A |  |  | Yes |  | Yes |  |  | Yes |  | Yes | [60 empty] | 5 | OEM Stationary - 4 Pole, right
| 6 |  | 6 | [6 empty] | 10 | 1000A |  |  | Yes |  | Yes |  |  | Yes |  | Yes | [60 empty] | 6 | OEM Stationary - 4 Pole, left | Yes | Yes
| 7 |  | 7 | EntelliGuard T (EGT) Non-Auto CB/Switch [1] |  |  |  |  | Yes | 12 | 1200A | [10 empty] | R | 75 | 105 | 50 | 50 | 42 | 100% | 42 | 42 | - | - | - | [36 empty] | T | T | T | T | T | T | T | T | T | T | T | T | 7
| 8 |  | 8 | [6 empty] | 13 | 1250A |  |  | Yes |  | Yes |  |  | Yes |  | Yes | S | 88.2 | 105 | 50 | 50 | 40 | 100% | 50 | 50 | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [29 empty] | 8
| 9 |  | 9 | [6 empty] | 16 | 1600A |  |  | Yes |  | Yes |  |  | Yes |  | Yes | C | 105 | 105 | 50 | 50 | 40 | 100% | 50 | 42 | - | - | - | [48 empty] | 9
| 0 |  | 0 | [6 empty] | 20 | 2000A |  |  | Yes |  |  |  |  | Yes |  |  | K |  | 143 | 65 | 50 | 42 | 100% | 50 | 42 | - | - | - | [36 empty] | T | T | T | T | T | T | [6 empty] | 0
| A | AEG Branded EntelliGuard G (ME10) | A | ANSI/UL1066 CB - F1 SSD, F2 & F3 TSD | [5 empty] | 25 | 2500A |  |  | Yes |  |  |  |  | Yes |  |  | N |  | 143 | 65 | 65 | 50 | 100% | 65 | 65 | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | [9 empty] | 2 | 2 | 2 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [17 empty] | A | GE Wind Stationary - 3 Pole [4]
| B |  | B | UL489 CB - F1 SSD, F2 & F3 TSD | [5 empty] | 30 | 3000A | [10 empty] | D |  | 143 | 65 | 65 | 40 | 100% | 65 | 40 | - | - | - | [48 empty] | B | GE Wind Stationary - 4 Pole, left [4]
| C |  | C | ANSI/UL1066 Non-Auto CB/Switch - F1 SSD, F2 & F3 TSD | [5 empty] | 32 | 3200A |  |  | Yes |  |  |  |  | Yes |  |  | H |  | 187 | 85 | 65 | 65 | 100% | 65/85[1] | 65/85[1] | 50/65[1] | 35/50[1] | 20/35[1] | [48 empty] | C | GE Wind Stationary - 4 Pole, right [4]
| D |  | D | UL489 Non-Auto CB/Switch - F1 SSD, F2 & F3 TSD | [5 empty] | 40 | 4000A |  |  | Yes |  |  |  |  | Yes |  |  | P | [59 empty] | D | GE Drawout - 3 Pole
| E |  | E | Entellisys CB | [5 empty] | 50 | 5000A |  |  | Yes |  |  |  |  | Yes |  |  | E |  | 187 | 85 | 85 | 85 | 100% | 85 | 85 | - | - | - | [48 empty] | E
| F |  | F | UL977 Fused Non-Auto CB/Switch (future) | [5 empty] | 60 | 6000A | [10 empty] | M | 187 | 220 | 100 | 100 | 85/100[2] | 100% | 85/100[2] | 85/100[2] | 65[3] | 50[3] | 35[3] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3 | 3 | [19 empty] | 2 | 2 | 2 | [14 empty] | F | GE Stationary - 3 Pole
| G |  | G | IEC CB |  |  | Yes |  |  | 64 | 6400A |  |  | Yes |  |  |  |  | Yes |  |  | B | [59 empty] | G
| H |  | H | IEC 100% Rated | [17 empty] | G |  | 220 | 100 | 100 | 100 | 100% | 100 | 100 | - | - | - | [8 empty] | 3 | 3 | [38 empty] | H
| I |  | I | [18 empty] | L | 220 | 330 | 150 | 150 | 150 | 100% | 100 | 100 | 65 | 50 | 35 | [20 empty] | 3 | 3 | 3 | 3 | [24 empty] | I
| J |  | J | IEC Non-Auto CB/Switch |  |  | Yes | [14 empty] | U | [59 empty] | J
| K |  | K | IEC Non-Auto CB/Switch 100% Rated | [17 empty] | V | [59 empty] | K
| L |  | L | UL489B DC Non-Auto CB/Switch * | [17 empty] | Y | [59 empty] | L | GE Drawout - 4 Pole, left (future)
| M |  | M | ANSI/UL1066 Non-Auto CB/Switch - F1 Only, TSD | [17 empty] | W | [59 empty] | M
| N |  | N | ANSI/UL1066 CB - F1 Only, TSD | [17 empty] | Notes: | [59 empty] | N
| O |  | O | [19 empty] | [1] Env. 1/Env. 2, respectively | [58 empty] | O
| P |  | P | GE Wind 1400V Breaker | [18 empty] | [2] Env.2/Env.3, respectively | [58 empty] | P
| Q |  | Q | [19 empty] | [3] F2 Only | [58 empty] | Q
| R |  | R | AEG branded retrofill (future) | [18 empty] | [4] Internally tested only. Not IEC certified | [58 empty] | R | GE Drawout - 4 Pole, right (future)
| S |  | S | UL489 Non-Auto CB/Switch - F1 Only TSD | [77 empty] | S | GE Drawout - 3 Pole Single Cluster [1]
| T |  | T | EntelliGuard T (EGT) CB [1] |  |  |  |  | Yes | [72 empty] | T
| U |  | U | UL489 CB - F1 Only, TSD | [77 empty] | U
| V |  | V | [78 empty] | V | GE Stationary - 4 Pole, right
| W |  | W | IEC Non-Auto CB/Switch w/MCR |  |  | Yes | [74 empty] | W | GE Stationary - 4 Pole, left
| X |  | X | [78 empty] | X | OEM Stationary - 3 Pole, No Rear Terminations
| Y |  | Y | GE Wind 1400V Switch | [77 empty] | Y | OEM Stationary - 4 Pole, Right, No Rear Terminations
| Z |  | Z | IEC Non-Auto CB/Switch 100% Rated w/MCR | [77 empty] | Z | OEM Stationary - 4 Pole, Left, No Rear Terminations
Notes:
[1] Specific Conditions apply only available when noted in "EGT" column. Only available for Digit 1 = "G"
SSD - Side-mounted Secondary Disconnect
TSD - Top-mounted Seconddary Disconnect

## AEG (ME10) Cassette Variant
Home
AEG Branded EntelliGuard G (ME10) Cassette Variant
| DIGIT 1 |  | DIGIT 2 |  |  |  | DIGITS 3, 4 |  |  |  | DIGIT 5 | [31 empty] | DIGIT 6 |  |  |  | DIGIT 7 |  |  |  | DIGIT 8 |  |  |  |  | DIGIT 9 |  |  |  |  | DIGIT 10,11 |  | DIGIT 12 |  | Complete IEC Cat #
| PRODUCT LINE DEFINITION |  | PRODUCT TYPE |  |  |  | CURRENT RATING |  |  |  | INTERRUPTION TIER (kA) and Frame Size | [31 empty] | CONSTRUCTION |  |  |  | CONNECTION MODE |  |  |  | POSITION SWITCHES |  |  |  |  | KEY LOCKS |  |  |  |  | FUTURE USE |  | DELIVERY MODE
| Character | Description | Character | Description | EGG | EGT | Character | Description |  |  | EntelliGuard G | [25 empty] | EntelliGuard T | [5 empty] | Character | Description | EGG | EGT | Character | Description | EGG | EGT | Character | Description | EGG | EGL | EGT | Character | Description | EGG | EGL | EGT | Character | Description | Character | Description
[5 empty] | IEC |  |  |  | EGG | EGT | IEC | [33 empty] | IEC |  |  |  | IEC |  |  |  | IEC |  |  |  |  | IEC
| 1 |  | 1 | [5 empty] | IEC |  | Character | Interruption Ratings | [10 empty] | Envelope Size by Rated Current | [19 empty] | 2 | OEM Drawout - 3 Pole | Yes | Yes | U | Rear Universal, T Stubs Rotatable for Horizontal or Vertical Buss | Yes | Yes | 2 | Set of 1 NO and 1NC contacts per Position | Yes | Yes | Yes | R | For 1 Ronis Key lock | Yes | Yes | Yes | XX |  | M | Mounted with Breaker
| 2 |  | 2 |  |  |  | 4 | 400A |  |  |  | Icm (kA) peak Isolator | Icm (kA) peak Breaker | Icu (kA) @ 230, 240, 400, 415, 440Vac | Icu (kA) @ 500Vac | Icu (kA) @ 690Vac | Ics (kA) % of Icu | Icw (kA) @ 230-500V | Icw (kA) @ 690V | Icw (kA) @ 250Vdc, 1 pole [4] | Icw (kA) @ 500Vdc, 2 poles [4] | Icw (kA) @ 750Vdc, 3 poles Ϯ | Breaker | [13 empty] | Breaker | [5 empty] | 5 | OEM Drawout - 4 Pole | Yes | Yes | F | Flat Front Access | Yes | Yes | 4 | Set of 2 NO and 2NC contacts per Position | Yes | Yes | Yes | S | For 2 Ronis Key locks | Yes |  |  |  |  | R | As separate component
| 3 |  | 3 |  |  |  | 6 | 600A | [14 empty] | Type AG | [11 empty] | Type AH |  | Type AT | [5 empty] | X | OEM Drawout - 3 Pole, No Rear Terminations |  |  | H | Rear Horizontal Buss |  | Yes | 5 | Carriage Position Switch - 1 NO/1NC power rated, 1 NO/1NC signal rated | Yes |  | Yes | P | For 1 Profalux Key lock | Yes | Yes | Yes
| 4 |  | 4 |  |  |  | 7 | 630A | [14 empty] | 400A | 630A | 800A | 1000A | 1250A | 1600A | 2000A | 2500A | 3200A | 4000A | 5000A | 6400A | 3200A | 4000A | 400A | 630A | 800A | 1000A | 1250A | 1600A | Y | OEM Drawout - 4 Pole, No Rear Terminations |  |  | V | Rear Vertical Buss | Yes[1] | Yes | 7 | Carriage Position Switch - 5 NO/1NC power rated (connect), 1 NO/1NC power rated (test & connect) |  |  |  | Q | For 2 Profalux Key locks | Yes
| 5 |  | 5 |  |  |  | 8 | 800A | [38 empty] | Notes: |  |  |  | X | None |  |  |  | T | 1 Ronis key lock shutter interlock | Yes |  | Yes
| 6 |  | 6 |  |  |  | 10 | 1000A | [39 empty] | [1] Available for AH type only | [7 empty] | U | 1 Profalux key lock shutter interlock | Yes |  | Yes
| 7 |  | 7 | EntelliGuard T (EGT) Switch ** |  |  | 12 | 1200A |  |  | R | 75 | 105 | 50 | 50 | 42 | 100% | 42 | 42 | - | - | - | [33 empty] | X | No Lock Prevision mounted | Yes | Yes | Yes
| 8 |  | 8 |  |  |  | 13 | 1250A |  |  | S | 88.2 | 105 | 50 | 50 | 40 | 100% | 50 | 50 | - | - | - | [5 empty] | 1
| 9 |  | 9 |  |  |  | 16 | 1600A | Yes | Yes | C | 105 | 105 | 50 | 50 | 40 | 100% | 50 | 42 | - | - | -
| 0 |  | 0 |  |  |  | 20 | 2000A | Yes |  | K |  | 143 | 65 | 50 | 42 | 100% | 50 | 42 | - | - | - | [14 empty] | T | T | T | T | T | T
| A | AEG Branded EntelliGuard G (ME10) | A | ANSI/UL1066 CB - F1 SSD, F2 & F3 TSD |  |  | 25 | 2500A | Yes |  | N |  | 143 | 65 | 65 | 50 | 100% | 65 | 65 | - | - | -
| B |  | B | UL489 CB - F1 SSD, F2 & F3 TSD |  |  | 30 | 3000A |  |  | D |  | 143 | 65 | 65 | 40 | 100% | 65 | 40 | - | - | -
| C |  | C | ANSI/UL1066 Switch - F1 SSD, F2 & F3 TSD |  |  | 32 | 3200A | Yes |  | H |  | 187 | 85 | 65 | 65 | 100% | 65/85[1] | 65/85[1] | 50/65[1] | 35/50[1] | 20/35[1] | [5 empty] | 1 | 1
| D |  | D | UL489 Switch - F1 SSD, F2 & F3 TSD |  |  | 40 | 4000A | Yes |  | P
| E |  | E |  |  |  | 50 | 5000A |  |  | E |  | 187 | 85 | 85 | 85 | 100% | 85 | 85 | - | - | -
| F |  | F |  |  |  | 60 | 6000A |  |  | M | 187 | 220 | 100 | 100 | 85/100[2] | 100% | 85/100[2] | 85/100[2] | 65[3] | 50[3] | 35[3] | [6 empty] | 2 | 2 | 2 | 2 |  | 3 | 3 | 3
| G |  | G | IEC CB | Yes |  | 64 | 6400A | Yes |  | B
| H |  | H | IEC 100% Rated | Yes | [5 empty] | G |  | 220 | 100 | 100 | 100 | 100% | 100 | 100 | - | - | -
| I |  | I | [7 empty] | L | 220 | 330 | 150 | 150 | 150 | 100% | 100 | 100 | 65 | 50 | 35
| J |  | J | IEC Non-Automatic CB (Switch) | [6 empty] | U
| K |  | K | IEC Non-Automatic CB (Switch) 100% Rated | [6 empty] | V
| L |  | L | UL489B DC Non Auto CB * | [6 empty] | Y
| M |  | M | ANSI/UL1066 Switch - F1 Only, TSD | [6 empty] | W
| N |  | N | ANSI/UL1066 CB - F1 Only, TSD | [6 empty] | Notes:
| O |  | O | [8 empty] | [1] Env. 1/Env. 2, respectively
| P |  | P | GE Wind 1600V Breaker | [7 empty] | [2] Env.2/Env.3, respectively
| Q |  | Q | [8 empty] | [3] F2 Only
| R |  | R | [8 empty] | [4] Internally tested only. Not IEC certified
| S |  | S | UL489 Switch - F1 Only TSD
| T |  | T | EntelliGuard T (EGT) CB ** |  | Yes**
| U |  | U | UL489 CB - F1 Only, TSD
| V |  | V
| W |  | W
| X |  | X
| Y |  | Y
| Z |  | Z
| Notes: |  | Notes:
|  | * See Variant |  | * See Variant
|  | ** Specific Conditions apply only when noted. Takes IEC Descriptions |  | ** Specific Conditions apply only available when noted.
SSD - Side-mounted Secondary Disconnect
TSD - Top-mounted Seconddary Disconnect